## Report
Numbers | meter_id | contact_date | failure_type | Faults | contact_type | connection_type | service water system | heating system | Comment Abbreviation | description | assessment | failure_start_date | failure_end_date | action | fp_report
0 | a794e2fc5e7067c68fba77306702f2c384c4d35733da8af0cc9d2e02e42e2bda | 2022-11-23 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 |  | Cooling. Suspicion of danfoss living in bedroom. | Proven |  |  | Error is resolved | /data/reports/71405276_20221123.pdf
1 | 4797f8e524f69d5b8e5e6798249e064d05d3199223bab30b36459bb066a0c6b5 | 2022-03-03 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2021-10-15 | 2022-04-06 | Customer contacts VVS
2 | 61aa241a9e89310aaedda04af4bb4bd342734434cca8c95ba8ea010b4907c6ca | 2022-03-03 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion | 2022-02-22 | 2022-06-17 | Customer contacts VVS
4 | 61aa241a9e89310aaedda04af4bb4bd342734434cca8c95ba8ea010b4907c6ca | 2022-03-03 | Pump failure | Pump failure | 2 | 1 |  |  |  |  | Suspicion | 2022-02-22 | 2022-06-17 | Customer contacts VVS
5 | 736f27250c0f3eb835f494212682f7860bbb3ef4785d2fac967ed65cfc204c84 | 2022-03-10 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Proven | 2021-12-01 | 2022-03-11 | Error is resolved
6 | f3e4638d1c66eb22319c2e5ef938cf7e8199c719fee648c5b33b0c814b910f09 | 2022-03-10 | Error in UFH master controller | Error in UFH master controller | 2 | 1 |  |  | UFH with no control | The reason was a small underfloor heating circuit without control. | Proven | 2021-11-30 | 2022-03-11 | Error is resolved
7 | 35fdd686494e5eb6c3fb024aeea36b6ca47c1a4dee8085b9dcec6402bc633354 | 2022-03-14 | Telestat in UFH | Telestat in UFH | 2 | 1 |  |  |  |  | Proven | 2022-10-20 | 2022-03-15 | Error is resolved
8 | 3702dcdc1d85736f0f9813dbbdbae87a1a8c7d758a61776b4cd4dcc33f8eda2c | 2022-03-14 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-01-24 | 2022-03-17 | Error is resolved
9 | 3702dcdc1d85736f0f9813dbbdbae87a1a8c7d758a61776b4cd4dcc33f8eda2c | 2022-03-14 | Other (DHW) | Other (DHW) | 2 | 1 |  |  | DHW - Valve | The problem is considered to be the valve for regulating the hot water. | Proven | 2022-01-25 | 2022-03-17 | Error is resolved
10 | a6ff2f38dd2e5ad56e5ce58fc7683845d841676397e4986f62a505dfc51018ff | 2022-03-14 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Suspicion | 2021-06-19 |  | No action
11 | 058f7d12d9b1bfda3dd916541e2db18fdf085adde0930a03254c8caa50afa837 | 2022-03-17 | Other (DHW) | Other (DHW) | 2 | 1 |  |  | DHW - AVTB valve | AVTB valve for controlling the hot water did not close down | Suspicion | 2022-12-15 | 2022-03-18 | Customer contacts VVS
12 | b2f64224e8e7e5546c7de2f90f68c0ea0dea2da50f60da3e8eb8eb50aea4e4cf | 2022-03-17 | Incorrect setting - Pump | Incorrect setting - Pump | 2 | 2 |  |  |  |  | Proven | 2022-01-29 | 2022-03-23 | Error is resolved
13 | bfdf1394d1ece5c32e6839edf9214fedad9f969fccbd376afd4159a792af6a8e | 2022-03-24 | Radiator valve | Radiator valve | 2 | 1 |  |  |  |  | Proven | 2022-03-10 | 2022-03-25 | Error is resolved
14 | 59e1d29cc131366f4ce1111b8e86519ea88d2592d24587f6ddc689ce7a1c767f | 2022-03-24 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Proven |  |  | No action
15 | 73e7600326be9a17831ef86bc896a9f661e0f7bbb91fbb5d5fb7e07906d4d2f2 | 2022-03-24 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Proven | 2021-11-29 | 2022-06-20 | No action
16 | bd29320cd6ddb79e8fed437ab64199212fa4d36284f2b0fd1ebba9ca03e57d5a | 2022-11-25 | Too small heating surfaces | Too small heating surfaces | 2 | 1 | 1 | 1 | Radiator smart thermostat turned up to max | Radiator on the 1st floor by the stairs. Too small heating surface. Smart thermostat turned up too high. Brochure about watts delivered. | Proven |  |  | Error is resolved | /data/reports/71078707_20221125.pdf
17 | 0870240ab7aff47830ad954ab5d010d5f0ab8258251bee0a55a4bde528813b1b | 2022-03-24 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 |  |  |  |  | Proven | 2021-11-04 | 2022-04-09 | No action
18 | 155c0bfd017353fb9e256d87e697d05596b4c985f4a9eadf040fde60fedf552c | 2022-03-24 | Towel dryer | Towel dryer | 2 | 1 |  |  |  |  | Proven | 2021-09-20 | 2022-03-25 | Error is resolved
19 | 13dc2b127b0cf5a4218fa91ec125ca1d85226455a36bba0b525de384ac48dc2c | 2022-03-24 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Proven | 2022-10-10 | 2022-04-21 | No action
20 | b4506bc721a42509febff199ee60eb26a33a4c9162496bdd185de230c39d6b3d | 2022-03-25 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Proven | 2021-10-31 | 2022-03-26 | No action
21 | 0e2200871604b173676ea89db91b8fa53e50297dcb1ade81db5a7613af07ccac | 2022-04-01 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Proven | 2021-12-13 | 2022-04-12
22 | a04e7e853040009edc76d3e596d75eacf2408c260d559c0ebb61097399c46151 | 2022-03-29 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion |  | 2022-03-30 | Error is resolved
23 | a04e7e853040009edc76d3e596d75eacf2408c260d559c0ebb61097399c46151 | 2022-03-30 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Proven | 2021-11-02 | 2022-04-04 | Error is resolved
24 | c81eb18d3ac7e47137708fcfa725a28408bc74ba74f47ab6348d5be25dfde075 | 2022-03-30 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion |  | 2022-06-25 | Customer contacts VVS
25 | 95d78ac977fc5f48c36aed3340b48d216136d5a18ac8c9854a467a59c3a9ea87 | 2022-03-30 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 |  |  |  | meter_id | Proven |  | 2022-03-30
26 | 95d78ac977fc5f48c36aed3340b48d216136d5a18ac8c9854a467a59c3a9ea87 | 2022-03-30 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven |  | 2022-03-31 | Error is resolved
27 | e19be7b5d8d8950bf9b2b311478c3d54b646965bca883121e37882b373b5ff89 | 2022-04-01 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Suspicion |  |  | No action
28 | d8e747b2d290cf9fc45b1b9fb20b9641ea98cbddf7e8050ff142de96e01dcf51 | 2022-04-01 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Suspicion |  |  | No action
29 | 826608ca2dffbeef49c3c3f7bde06f1c63ae9b9e8ec3acf45d8ec25a55f2290f | 2022-04-01 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-03-24 | 2022-04-19 | Customer contacts VVS
30 | 3a47dce0d8f4521e2927c183f141976d1017fb0f263899fcea169196403db3d9 | 2022-04-04 | Telestat in UFH | Telestat in UFH | 2 | 1 |  |  |  |  | Proven | 2022-01-21 | 2022-04-04 | Customer contacts VVS
31 | c2137f1e5bce5fe5089c8f3a14ec4e7d1873c253253ef7c68a59ad7d6d8d01cb | 2022-04-05 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 |  |  |  |  | Suspicion | 2022-03-10 | 2022-04-07
32 | c2137f1e5bce5fe5089c8f3a14ec4e7d1873c253253ef7c68a59ad7d6d8d01cb | 2022-04-05 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Suspicion | 2022-03-10 | 2022-04-07 | Error is resolved
33 | 56e5bbdd1fc6751d841eea15c71d2fdf16adb553122b41159a1367c1de15785c | 2022-04-06 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Proven |  |  | No action
34 | 28042e6d469aa6b189289adf47d03048b7ba693ac9ca02a28847d0404106ea87 | 2022-04-06 | Other (SH) | Other (SH) | 2 | 1 |  |  |  |  | Suspicion | 2022-04-15 | 2022-04-30 | Customer contacts VVS
35 | 44365f43fffd96cb702be37af262f097a15201cd4e2b4d5df2804b45687c4986 | 2022-04-27 | Other (DHW) | Other (DHW) | 2 | 1 |  |  |  |  | Suspicion | 2022-04-20 |  | Customer contacts VVS
36 | 3ad3d92a50ce6cff63621a3dd1330ff48d360934774d742a0c558e4bbe8c0508 | 2022-04-27 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion | 2022-04-15 | 2022-04-29
37 | 3ad3d92a50ce6cff63621a3dd1330ff48d360934774d742a0c558e4bbe8c0508 | 2022-04-28 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 2 |  |  |  |  | Suspicion |  | 2022-05-16
38 | b847da44eb6d33722ec11d94ff06f0e1a23c04c0e3dbfc0e77d4c92a3b076a0a | 2022-04-28 | User behaviour | User behaviour | 2 | 2 |  |  |  |  | Proven | 2021-10-21 | 2022-05-21
39 | 4f6504803dd1b46d91799e9a69bcb9f6323939c38f6a15824aacd9d69426f8e0 | 2022-04-28 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Proven | 2022-04-19 | 2022-05-12 | Customer contacts VVS
40 | 8de206772c3bc65218066df43a0b2cc8488c8afad24ef8d32cb24c41f4182662 | 2022-04-28 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion | 2022-02-18 | 2022-05-19 | No action
41 | 385efb860c974a7175ec9fabd39aa7cf50474713b8fbe3f19d59a5b50fbae922 | 2022-04-28 | Other (SH) | Other (SH) | 2 | 1 |  |  |  |  | Suspicion |  | 2022-05-07 | Customer contacts VVS
42 | 1c29f3e59d35a1187487b58a15c3e2391b6a60e85637a844751ca6a68d9fc498 | 2022-04-28 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion |  | 2022-05-06 | Customer contacts VVS
43 | 2891487930a5beb647a3de7a761a582751f074197b39fc1f607bc88f04645846 | 2022-04-28 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion | 2022-04-29 | 2022-05-06 | Error is resolved
44 | 4bb264fdd79313dfca5b743ec405cf2954cea46983c3973ad6b63fa8e601f867 | 2022-04-28 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-04-05 | 2022-05-06 | Customer contacts VVS
45 | 6c8686bd3de7e23f479950fc147d2080cc8a6793e5a6ca38e93e801a44123b4e | 2022-04-28 | Telestat in UFH | Telestat in UFH | 2 | 2 |  |  |  |  | Suspicion | 2022-04-08 | 2022-05-07 | Error is resolved
46 | 741eef915029cd52bf302088394d4de39c285c49c2a3fa456faf4615a8acffe0 | 2022-04-28 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 2 |  |  |  |  | Suspicion | 2022-04-21 | 2022-05-12 | Customer contacts VVS
47 | 902cece2f89ec409b9da64f5ff4ca30cfb9efabd0da0d2b79b5617c7032218db | 2022-04-28 | UFH shunt | UFH shunt | 2 | 2 |  |  |  |  | Suspicion |  | 2022-05-14 | Customer contacts VVS
48 | d9ff179f2a4d88b85beb07cda4519a0def9679da4ac0531d5eb62f23f1c02921 | 2022-05-11 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion | 2021-11-26 | 2022-05-13 | Customer contacts VVS
49 | b0a449e0bb1a5cbd9fdb0a50d80e225140c435bf96b5d39d39020a47a5026c22 | 2022-05-11 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven |  | 2022-05-14 | Error is resolved
50 | 8ca003f55c1cda082fca1b77b6421a08b98dda239e2a8d9262d2884784328f1f | 2022-05-11 | Telestat in UFH | Telestat in UFH | 2 | 1 |  |  |  |  | Suspicion |  | 2022-08-27 | Customer contacts VVS
51 | 6970460297308b36e8667281ae12ab00ab5bf04585d1a9415488c82c9c4cf8d5 | 2022-05-11 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion |  | 2022-05-16
52 | 1d29fb0b5f986a4ea5ca0f3c09b86fd700568538d8443b31bd60cff44cc73ac4 | 2022-11-28 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Radiator turned all the way up - User behaviour | Uninhabited house that was for sale. Homeowner's mother returned (note in mailbox) Review of installation. It is estimated to be the radiator on the bathroom living room floor that was turned up too high. Recommended to install watts to follow consumption. | Proven |  |  | Error is resolved
53 | c78997d3a602678850cb84fd1c7e10ea94a1d4f1be4cdfe251c522e41dad024c | 2022-11-28 | User behaviour | User behaviour | 2 | 1 |  | 3 | Regulation of UFH and Hot Radiator - Space Heating | Cooling. Review of facilities. It is estimated to be manually regulated underfloor heating in the bathroom basement and the radiator in the kitchen which was too high. | Proven |  |  | Error is resolved
54 | d8dd648a4334b9e8ab5742e2b8e75bc569e545a32b499d49b898af1598d58cdb | 2022-11-12 | Other (DHW) | Other (DHW) | 2 | 1 |  |  |  |  | Suspicion |  | 2022-05-14 | Customer contacts VVS
55 | b09d6560e86a328c1e10b33dff5011c71366a85e3e4a62ccc0749ea0afc3be3c | 2022-11-29 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Radiator turned all the way up - User behaviour | House under renovation. The owner contacted and we agreed to meet. It was a couple of radiators that were turned up well. Recommended to install watts to follow consumption. | Proven |  |  | Error is resolved
56 | 5868d2ba1b86ce5d71794b3f9ab4c739708676d6612728103d78c3a58efe5578 | 2022-11-29 | User behaviour | User behaviour | 2 | 1 | 1 |  | Radiator turned all the way up - User behaviour | House under renovation. Meet the owner at home. They have had water damage and radiators were maxed out. up. There was no thermostat installed yet. Recommended by get these fitted. Recommended to install watts app. | Proven |  |  | Customer contacts VVS
57 | 4ce2f565d5a375ddd12d58de94b2592a6ce4e9dad55f671fb9da55d5f52968e5 | 2022-12-01 | User behaviour | User behaviour | 2 | 1 | 1 | 1 | Radiator turned all the way up - User behaviour | Increasing consumption and poor cooling. The customer has set the radiators in the living room high. The customer requires more heat in the home than normal. In addition air is released without closing all thermostats in the living room. (the radiator is closed under the window which is vented by) User behaviour discussed with the customer. | Suspicion |  |  | No action
58 | 06d932cda45f20d2f2365324715e0d916321c7c2726725cca6f9cf24ee817a83 | 2022-12-01 | Telestat in UFH | Telestat in UFH | 2 | 1 | 1 | 2 | UFH Shunt | Cooling. Peaks during periods of poor cooling. Suspicion of UFH shunt. Show him what to look out for. Will contact VVS as recently installed room telestat may not have contact to master unit. DHW temp. adjusted down a bit. | Suspicion |  |  | Customer contacts VVS
59 | 450f312cddda779b4399e317e842abf7173924b9d261cee615089d01a94e7870 | 2022-12-02 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Radiator turned all the way up - User behaviour | Cooling. Review of facilities. Nice cooling when visiting. Asked about the use of radiators. The consumer said that there was a radiator that was sometimes turned up a lot. Explained that it was better to have some heat on all radiators. Got a printout of consumption and cooling over the most recent period. She was happy about that and gave a good understanding. Brochure about watts delivered. | Suspicion |  |  | Error is resolved
60 | e8a43b300f8a100a81d9058abb2271f072e714a3aa869c54229a0c898333c615 | 2022-12-02 | User behaviour | User behaviour | 2 | 1 |  |  | Radiator turned all the way up - User behaviour | Periodically increasing consumption and poor cooling. Bathroom etc. under renovation. In this connection the door and window have been open for periods. This has affected radiator thermostats and the customer has not thought about it in the situation. Good dialogue and discussion regarding good heating advice. | Suspicion
61 | d08c651eefdd95ef97050f4ba54db5152d56ffb8a13840b6681be4fe1bad48c8 | 2022-12-02 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 | 2 | 3 | VVB - Storage tank - Radiator turned all the way up - User behaviour | VVB was set at 70 degrees. Recommended to adjust it down to 55. Explanation to use all radiators in the rooms that have heat. Printout of consumption and brochure about watts app provided. | Proven |  |  | Error is resolved
62 | 86f06bcfe6a108bc2b2b0240777aa787588e76aa652cdaf0443ecd152726b367 | 2022-12-05 | User behaviour | User behaviour | 2 | 1 | 2 | 1 | Poor Cooling - User behaviour | Poor cooling. On visit flow 27 L/h and delta T = 34 degrees. User behaviour possibly the cause of intermittent poor cooling (when ventilating the home - opening and closing radiators) Good heating advice discussed with the customer. Meter readings reviewed with customer. | Suspicion
63 | 02199b644777bc868658da678e73c27469641d881d8a5322a7bbf952f93439b2 | 2022-12-05 | Other (SH) | Other (SH) | 1 | 1 | 1 | 1 | Faulty radiator valve | Solenoid valve for radiators does not close. | Proven | 2022-10-26 | 2022-12-05 | Error is resolved
64 | 91e768527db5e1a40de05f0591cc466aaf78c644b74d21c479185850bc926604 | 2022-12-06 | UFH shunt | UFH shunt | 2 | 1 | 1 | 2 | Poor Cooling: UFH Shunt | Possibly UFH shunt cause of increasing/fluctuating consumption and hence poor cooling. The customer contacts the supply for any service scheme registration. | Suspicion
65 | ce3f27a747d407c08d29cf21fc36b77c1428c64b73a22d70624eee65834e96e3 | 2022-12-06 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Poor Cooling: User behaviour of radiator | Possibly User behaviour. Periodically large flow with poor cooling. High setting/opening of radiators after venting as well as opening after shutting down for the night in the conservatory possibly causing poor cooling. Good heating advice and User behaviour discussed with the customer. Follow-up next week with contact to customer. | Suspicion
66 | a954357d9b5dda8be0c466e1999d0b6340ca91026c167da7b92b27f7cfd9f7cc | 2022-12-07 | Return thermostat set too high | Return thermostat set too high | 2 | 1 | 1 | 1 | Poor Cooling: New UFH control (wavin) | Visit due to periods of poor cooling. The problem has arisen in connection with the installation of a new underfloor heating control (Wavin) Room temperature is a good 2 degrees higher than set point. Will contact VVS for review. Contact later to have a new basket sent. Recommended to install watts. | Suspicion |  |  | Customer contacts VVS
67 | 9e7356aee06b085d81e588e155506872616552ffdb8c364f0199a9cbd826014d | 2022-12-07 | Towel dryer | Towel dryer | 2 | 1 | 1 | 2 | UFH - Towel dryer | Cooling. Newly renovated house with underfloor heating. It is estimated to be a towel dryer that was turned up to max. This closed down and consumption fell significantly. Better cooling. Recommended to install watts to follow consumption. | Proven |  |  | Error is resolved
68 | 87315ee6811e612a6fececeb2f211a8be0149c93e1bb8f062c6404e5b0f98f80 | 2022-12-13 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Radiator turned all the way up - User behaviour | Cooling. 600 l/h delta t 10. Review of plant. It is considered to be a radiator that is set too high. Recommended to use all radiators instead. Review of meter about what it shows. Have installed watts. Have the house next door and want to go through it myself. Will contact later about new graph. | Proven |  |  | Error is resolved
69 | 4c3ba337bc21a59734a90044dac83b6ebbf375b34731f8719256917b169135a3 | 2022-12-13 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Smart Thermostat faulty | Cooling. Review of facilities. It is estimated to be a smart thermostat (unknown brand) on the 1st floor that is not working properly. This is recommended to be replaced. Consumer recommended to contact VVS. Recommended to have watts installed on the phone to monitor consumption. | Proven |  |  | Customer contacts VVS
70 | 142d5ed1c55931625dfe8d3076a9d53bb908ab744caa52000a848329687eb2be | 2022-12-15 | UFH shunt | UFH shunt | 2 | 1 | 1 | 3 | Poor Cooling: ECL - UFH Shunt and Radiator - Space heating -Defective valve | Heating + customer with poor cooling. Review of ECL and plant. Older house with radiators and underfloor heating in the bathroom. The UFH shunt for the bathroom is considered to be the cause. Possibly defective versus valve. Customer informed. Recommended to get watts. Curve about temp. and flow delivered. Would like to have a new basket sent later. Make inquiries yourself. | Proven |  |  | Customer contacts VVS
71 | 9858e0611fdd0577d51ba21535564075554503a18de103478d6e1940ec30afcb | 2022-12-15 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Radiator Thermostat - DHW Valve | Cooling. Inspection of the facility together with the owner. House under renovation. It is estimated to be the thermostat on the radiator in the living room that clicked off. They had just had the floors treated so it may have happened in that connection. Valve for controlling the hot water possibly defective. The hot water was very hot. Plumbing connected. Recommended to get watts. | Proven |  |  | Customer contacts VVS
72 | d98994a3cbcc75528404c8ceabef5fafe6f7ee890a1e21a5e1010966d197bddd | 2022-12-19 | Pressure differential regulator | Pressure differential regulator | 2 | 1 | 1 | 1 | Poor Cooling: High TD (pressure differential regulator) | Cooling. High consumption and lack of cooling. It is a FDF cabin. Review of facilities. TD was high and this recommended to be turned down to around 0.1 bar. Recommended to have watts installed to monitor consumption. | Proven |  |  | Error is resolved
73 | 3e9b56e40dca7de1a4bb59cc63b7744aa490ab29b7b2dcf746b76cc9b1892895 | 2022-12-20 | Other (SH) | Other (SH) | 2 | 1 | 1 | 1 | Space heating : stuck pipes | Have renovated the house. There are two heating pipes running up to the first floor. They are very hot and the customer said they were connected? (possible rotation) Will take up plumbing. Will contact you later to have a new basket sent. | Suspicion |  |  | Customer contacts VVS
74 | 3a1a90ae4bf4f8a4d238adfe44a1ac6bca88d21fcb68624d8777d1ebeeee8a84 | 2022-12-20 | Other (SH) | Other (SH) | 2 | 1 |  |  |  | Calorify unit. | Suspicion |  |  | Customer contacts VVS
75 | b91778d2470f4cf570b5accc6a65308a61bb216eb6f7a62fe88b4c60bdddb4a3 | 2022-12-20 | Towel dryer | Towel dryer | 2 | 1 | 1 | 1 | Poor Cooling: Towel dryer was too high | Very hot towel dryer probably causes increased consumption as well as poor cooling. | Suspicion
76 | 007bd83dd21628fa402c2215e390190cf49c198f991dc766d154cc02efb4c5ff | 2022-12-20 | Other (SH) | Other (SH) | 2 | 1 | 1 |  | Space heating: Radiators | Cooling. The house is heated by older heaters that send hot air around in ducts for heating and underfloor heating in some rooms. Have just installed smart thermostats in the house and it is in this connection that the cooling has become bad. The thermostat that opens the heat to the hot plate does not respond properly. Will contact those who have installed systems. Contact later to get a new basket. |  |  |  | Customer contacts VVS
77 | 7070bd3bc26387d57c4bedd7a13b4c3cdacf2b78c2e688d08bc7f08f91a30ccd | 2022-12-21 | Other (SH) | Other (SH) | 2 | 1 | 1 |  | Poor Cooling: DHW and Heatingfans | Cooling. In periods of high consumption and poor cooling. House has had a new utility water exchanger installed. The house is heated with two air heaters with a built-in heating circuit. It is estimated that the cause of poor cooling is there. Made the consumer have calorifiers call for heat and consumption increased to over 800 l/h. Will call the ventilation company. | Suspicion |  |  | Customer contacts VVS
78 | e9543964f9eb8c6e75d859f302950d86bfd20e89c3642d3c3a0e5f458f24fb7f | 2022-12-22 | Other (SH) | UFH shunt | 2 | 1 | 1 | 3 | Poor Cooling: UFH Shunt | Poor cooling high consumption. 250 l/h delta t 7. Review of plant. It is in connection with the new UFH shunt being put into use. This could be shut off and flow dropped to 40 l/h and 35 degrees delta t. Customer contacts the plumbing company. | Proven |  |  | Customer contacts VVS
79 | b748575f4592b3119e3c3c4bbe123de4d8497457e441939cc1014c6034ad20f1 | 2022-12-22 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Space heating: UFH Shunt stuck valve and Radiators | Cooling. Review of facilities. Combined underfloor heating and radiators. UFH shunt where the valve was stuck open. The customer will contact the plumbing company for service on plumbing installation. | Proven |  |  | Customer contacts VVS
80 | d5de970fad49da2b973b775af5b1c6fd95c8f3ad1f3225aaab4df8ed80ea0cbf | 2023-01-02 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 2 | 2 |  |  | Suspicion |  |  | Customer contacts VVS
81 | f3d037c3084aff68a1b34dad64d9b97503a0e497340f8e7c3ba5cfc2f1584c62 | 2023-01-02 | Other (SH) | Other (SH) | 2 | 1 | 1 |  | Poor Cooling: High set valve-heating system | Air heating system!. Increasing consumption and poor cooling. Possibly high set valve to control temp. for air heating installation cause of poor cooling. New visit arranged for tomorrow with partner. | Suspicion
82 | de533a9dc7120f34fcdb04c5f425b3e96e2336a9dc18d3841c7ad30659d8d8e9 | 2023-01-02 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 2 |  |  | Proven |  |  | Customer contacts VVS
83 | dabd6d4a693e52d3cb5a5f36abe3ea28ffaa54e2c68221ad9505d66a66c1e971 | 2023-01-03 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Poor Cooling: Bypass valve-spaceheating | Cooling. The house is used as a summer house. Consumer has installed smart thermostats and one of them had run out of power. Bypass valve was at 5 recommended around 3. Brochure on watts provided. | Proven |  |  | Error is resolved
84 | c20edbaf5469d1aea19a33aac6e221c4fbd0284632a6b4992f0f46cec5fc06f5 | 2023-01-03 | Pump failure | UFH shunt | 2 | 1 | 1 | 3 | Poor Cooling: UFH Shunt | Cooling. Review of facilities. Radiator fine cooling. Mini shunt closed and return temp dropped significantly. It is presumably the UFH shunt that is the cause of the lack of cooling. Consumers will take up plumbing. Brochure on watts and consumption graph provided. Will contact you later for a new graph. | Proven |  |  | Customer contacts VVS
85 | 76001eb5f87115eeef141315abf149c53132308ad835403e28c64ffbcfe46221 | 2023-01-03 | Other (SH) | Other (SH) | 2 | 1 | 1 | 2 | Poor Cooling: Pump - Bad TD and bad pipes for KV and VV | Cooling. TD was wrong. Pump set. The consumer is considering signing up for the service scheme. Recommended to have pipes changed for KV and VV due to corrosion. Will be in touch to get a new basket sent in a few months. | Proven |  |  | Customer contacts VVS
86 | 3287aad78008ab97870ae749b996befe6824c4d296c9dcc4322ece3fa9651ab4 | 2023-01-04 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Poor Cooling: User behaviour - Radiator and DHW AVTB | Cooling. Review of facilities. It is considered to be User behaviour regarding the use of the radiator in the living room. Recommended to use all radiators instead of one. AVTB on the exchanger was high but regulation was not possible because the handle was defective. The consumer said that the house had to go through a major renovation and a new exchanger and heating system were added. Had watts installed. | Proven |  |  | Customer contacts VVS
87 | 4ede3a2fa11cc29a39fb1b435fc5dcb1c6aaee7c3c8e896be2a03e5df3914465 | 2023-01-04 | Other (SH) | UFH shunt | 2 | 1 | 2 | 3 | Poor Cooling: Space heating - UFH Shunt | Cooling. After they were made aware of the lack of cooling they contacted VVS which has a rep. UFH shunt. Brochure on watts and consumption graph provided. | Proven |  |  | Customer contacts VVS
88 | e0e545aad48fd75406d8542537c9dafbfb42bb9528cf1995303fdcaf9b16b70f | 2023-01-04 | Other (SH) | Other (SH) | 2 | 1 | 2 | 3 | Poor Cooling: Space heating - UFH | Cooling. Review of facilities. It is estimated that the radiator in the pit under the window and the underfloor heating in the entrance hall are the cause. Will sign up for the service scheme. Recommended to get watts installed. | Suspicion |  |  | Customer contacts VVS
89 | 77aef7bfa95a5bce27b1f4f7fa6c931f40e3670fdbb67e8dc8c923117c40dffb | 2023-01-04 | Towel dryer | Towel dryer | 2 | 1 | 1 | 3 | User behaviour: Towel dryer | Consumer was on vacation in Taiwan but family could close up. It was the towel dryer that was the cause. Recommended to install watts to follow consumption. | Proven |  |  | Error is resolved
90 | e0ec7d6ae240b69293914b11591ab76ef2d8f274207edf354933337ae467f1f1 | 2023-01-05 | Other (SH) | Other (SH) | 2 | 1 |  | 3 | Poor Cooling: Space Heating - Radiator and heating fan | Cooling. Review of installation. Radiators and heaters. A calorifier was without control over the heat and this resulted in a lack of cooling. General heating advice discussed. Got watts installed on phone during visit. Would like to get another curve later to see if it has improved. | Suspicion
91 | 1e222ae5110c5f2116735b572d8f170e92903cb8cddc35ef62ba73adb267583b | 2023-01-05 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Space heating: Radiator turned too high | House under renovation. Radiator in kitchen set high resulting in insufficient cooling. (flow = 79 L/h and delta T = 20 degrees) When the radiator was shut off the flow dropped significantly. The customer goes through the installation himself and returns if necessary. back for new talk. | Suspicion
92 | c1e963596523c05dc73a143623c1d6a5190512002e0d0e5b793657a5e6a95ce6 | 2023-01-05 | Other (SH) | UFH shunt | 2 | 1 | 1 | 2 | Poor Cooling: Space heating - UFH Shunt | Cooling. It is estimated to be the hot water and UFH shunt causing the lack of cooling. Consumer will contact vvs for service on installation. | Suspicion |  |  | Customer contacts VVS
93 | 8c48d1c952c6c3734214ff8ab3ab35532a3cbc4bae71334c90dc9c444d82b544 | 2023-01-06 | Other (SH) | Other (SH) | 2 | 1 | 1 | 1 | Poor Cooling: Space heating - Radiator Valve | Cooling. 1 string plant. Valve in exchanger adjusted down and radiators adjusted. Contact for new basket later. Recommended to get watts installed. | Suspicion |  |  | No action
94 | 6b4403a7dd11dac25f46829590e8f2492ab68d99a1c6bf0824c12909e28b8fe3 | 2023-01-09 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 | 2 | 3 | Storage tank: AVTB and damaged sensor | Periodically increasing flow with poor cooling as a result. Possibly AVTB valve with damaged sensor element cause of poor cooling. Customer will replace this. | Suspicion
95 | 45976ae3aee99493cd1f0921cf3b64384b76077a43d0b8e67443628ffcfc8c01 | 2023-01-10 | Other (SH) | Other (SH) | 2 | 1 | 1 | 2 | Poor Cooling: Space Heating-Towel dryer and UFH | Cooling. Review of facilities. It is estimated to be a towel dryer in the bathroom. Bathroom has to go through a renovation in the near future) And a manually regulated underfloor heating in the living room that is the cause of angling cooling. Consumer recommended to install watts. Informed about the possibility of heat+. General heating advice discussed. | Proven |  |  | No action
96 | da5fc6e54127d07952ada9858f31261a14af9360e7acff0f89c800ddf9b204da | 2023-01-11 | UFH shunt | UFH shunt | 2 | 1 | 1 | 2 | Check Valve - UFH | Fluctuating consumption as well as poor cooling. Customer has had a visit from VVS. VVS believes that it is possibly the non-return valve at the mixing loop for the underfloor heating system that is the cause of fluctuating consumption and poor cooling. The customer is waiting for a new visit by the plumbing company to replace the component. | Suspicion |  |  | Customer contacts VVS
97 | 92741cf8d898974b6045a5e597acf5a4c56c679b20e67538b96f639a1edb51bf | 2023-01-11 | Radiator valve | Radiator thermostat | 2 | 1 | 1 | 3 | Poor Cooling: User behaviour | Cooling. Consumer was in the Faroe Islands but family could close up. After reviewing the system it was a smart thermostat that had run out of power. | Proven |  |  | Error is resolved
98 | dac015b802b0d3c5dd58aa9a96f7e48bcf1d277cf6df21420209fc26f9c7d4a7 | 2023-01-12 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Poor Cooling: Storage tank - AVTB and damaged sensor AND UFH check valve (space heating) | Cooling. In periods of lack of cooling. Review of facilities. AVTB stood a little high. Consumer recommended to adjust it to 3. Underfloor heating return valve on 1st floor adjusted down. Recommended to get watts installed on mobile. Get in touch later to see if measures have had an effect. | Suspicion |  |  | No action
99 | e773210e9a43e591f1181a3e2a1efcf89d916ae80b73bfd67fc4a9b22a20ca68 | 2023-01-12 | Other (SH) | Other (SH) | 2 | 2 | 2 | 1 | Poor Coooling: Storage tank-VVB and corrosion in the pipes | Cooling. Review of facilities. Indirect 1st string plant. The temperature had been turned up high. secondary side. Consumer had adjusted down again. Consumer informed about corrosion under VVB and pipes under this. Recommended to get service / rep. of plumbing. Informed about heating + and service arrangement. Review of meter display | Suspicion |  |  | Customer contacts VVS
100 | a590b3234af700db4a0dddb0ea3b9cb5aea81bad25850b0b485641773e626ca7 | 2023-01-12 | Other (SH) | Other (SH) | 2 | 1 | 2 | 3 | Poor Coooling: space heating | Cooling. Review of facilities. Former workshop with office and bathroom facilities. It is estimated that the heater in the workshop is the cause. This closed off and consumption fell. Review of meter and how to read it. | Proven |  |  | No action
101 | 76db1bd91b088ef399be98538776fe47ec493ec83df80cef708320b6be183da6 | 2023-01-13 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Heat Exchanger: Possibly check valve or regulating valvee | Cooling. House from 2015. Consumer said there had been several problems errors or deficiencies. Review of installation. Fine cooling radiators 1st floor. Hot water temp. 52 degrees. Recommended 48 degree furthest tap point. UFH shunt. Possibly defective versus valve / control valve. Pump was on 3. Recommended constant pressure. Consuming shown how. Considering signing up for the service scheme. I would like a new basket when I have had a visit from the plumbing. | Suspicion |  |  | Customer contacts VVS
102 | 1767efa761fb090fb3a6f5d11b10f49924311c41e03a4a4c021097221aef8d38 | 2023-01-13 | User behaviour | User behaviour | 2 | 1 | 1 | 1 | User behaviour: Radiator fully open | English speaking customer!! Fluctuating/large consumption and insufficient cooling. Large radiator in the living room was fully open (very hot). Customer recommended to contact VVS for review of installation (corrosion etc.) | Suspicion |  |  | Customer contacts VVS
103 | 8d3b0c9e617c36add93f91fece9d9478d409f2b26f96837f1ca93f8b133056cc | 2023-01-13 | Radiator thermostat | Radiator thermostat | 2 | 1 | 2 | 1 | Poor Cooling: Faulty Radiator thermostat | Cooling. The cause was a faulty thermostat in the entrance hall. Will contact caretaker. | Proven |  |  | Customer contacts VVS
104 | 7e6cc415fe5dca185a95786dfa57a9f45780acb1681f864f8ea364e5fadecd28 | 2023-01-04 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 | 1 | 3 |  |  | Suspicion
105 | 7e6cc415fe5dca185a95786dfa57a9f45780acb1681f864f8ea364e5fadecd28 | 2023-01-04 | Summer valve | Summer valve | 2 | 1 | 1 | 3 |  | overwrite report | Proven
106 | 7e6cc415fe5dca185a95786dfa57a9f45780acb1681f864f8ea364e5fadecd28 | 2023-01-17 | Summer valve | Summer valve | 2 | 1 | 2 | 2 |  | test updated | Proven
107 | 7e6cc415fe5dca185a95786dfa57a9f45780acb1681f864f8ea364e5fadecd28 | 2023-01-17 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 | 2 | 2 |  | error 2 - updated | Suspicion |  |  | Customer contacts VVS
108 | 51d32651eddd30ed68be1d4c9230edaa622f7dc5d5b84c078f1879dcd3b3a2b9 | 2023-01-18 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | User behaviour: Radiator fully open | Cooling. Review of facilities. It was radiators in the basement that were too high. AVTB on the hot water adjusted down. The customer had just installed the Watts app to monitor consumption. General heating advice discussed. Curve of consumption provided. | Proven
109 | b3e170621c0ac57193ab94a34666eb0d2c67d34dc0ed5f288040c2ed42ef7ae0 | 2023-01-18 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Poor Cooling: Space heating | Cooling. Radiator by kitchen adjusted down. Radiator under window in living room adjusted identically. Floor heating in bathroom turned down a little. Basket delivered. | Suspicion |  |  | No action
110 | be7bc69794dc28aa925ddf67d706ee213b97bfe7b9ddb900d7caf8fcdb3030ab | 2023-01-20 | Towel dryer | Towel dryer | 2 | 1 | 1 | 3 | Poor Cooling: Towel dryer was too high | Cooling. Customer was on holiday but brother could open up. It was a towel dryer in the bathroom that was screwed up. The customer's brother switched it off and consumption dropped significantly. Return about 35. Recommended to get watts installed on phone. | Proven
111 | 57090b9894af9ca95e6b6d8c5bdaf97348ed206277bbacbedc95023aa87c8f06 | 2022-05-12 | Radiator valve | Radiator valve | 2 | 1 |  | 3 |  |  | Proven |  |  | Error is resolved
112 | 5a81995fa71b666045e0d6354a24f0e9c8a6a6ba9996f37dc5206519ca9e7b38 | 2023-05-16 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion |  |  | No action
113 | 7e6cc415fe5dca185a95786dfa57a9f45780acb1681f864f8ea364e5fadecd28 | 2023-01-18 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 | 1 | 2 |  |  | Proven |  |  | Error is resolved | /data/reports/71083493_20230122.pdf
114 | 7e6cc415fe5dca185a95786dfa57a9f45780acb1681f864f8ea364e5fadecd28 | 2023-01-22 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 2 |  |  | Suspicion |  |  | Error is resolved | /data/reports/71083493_20230122.pdf
115 | f5564ced650fddaa3a591126fc76e7223279e418a33acd7f7c49feb84068ea66 | 2023-01-23 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | UFH manual valve control | Manual underfloor heating in the bathroom | Suspicion |  |  | Error is resolved | /data/reports/71871796_20230123.pdf
116 | f5564ced650fddaa3a591126fc76e7223279e418a33acd7f7c49feb84068ea66 | 2023-01-23 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Radiator temp set too high | Cooling. Radiator in the living room. Radiator hides mounted around. Turned up too high (Susen) | Proven |  |  | Error is resolved | /data/reports/71871796_20230123.pdf
117 | c4c3bfb859012b98d4339f2f396f053167f455b3bb8580db5ab632ac4309ac2f | 2023-01-23 | Lack of pressure on secondary side (indirect connection) | Lack of pressure on secondary side (indirect connection) | 2 | 1 |  |  | Storage tank out of operation | Cooling. Water shortage secondary side. but has its own waterworks and it is currently out of operation. | Suspicion |  |  | Customer contacts VVS | /data/reports/71338167_20230123.pdf
118 | 642b85763119f5076325504319270c8c332b158023cd334d87c2f0cf1a2ba6bc | 2023-01-23 | Too small heating surfaces | Too small heating surfaces | 2 | 1 | 1 | 3 | Too small radiator | Two radiators in the kitchen-dining room one of which with possibly too small a heating surface stood a little high. When shutting off this radiator flow decreased by approx. 100 L/h and cooling stabilized. The customer initially tries to set the two radiators for the best possible cooling. A new graph will be sent to the customer in approx. one month. Meter readings reviewed with customer. | Suspicion |  |  |  | /data/reports/71586475_20230123.pdf
119 | 05a5adb230000bdeef400c594ba784febff814bfe9660a4aa0878367f0361d4a | 2022-09-23 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Proven | 2022-09-22 | 2022-09-23 | Error is resolved
120 | 05a5adb230000bdeef400c594ba784febff814bfe9660a4aa0878367f0361d4a | 2022-06-14 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Suspicion | 2022-06-10 | 2022-06-14 | Error is resolved
121 | 2f3740da7be440154e229acc0fcfc43cea31edd6361088ee5c9ebcf98578e9da | 2022-06-14 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Proven | 2022-07-06 | 2022-07-08 | Error is resolved
122 | f06b27d28933023bdaa22a9045f4300955717c55415071907d0cbf595be958a4 | 2022-07-12 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Proven | 2022-07-08 | 2022-07-12 | Error is resolved
123 | db3ae2a6cd5345370701e0ba26760d45c1e15d798e27d1c5b9ca01704ba2ce05 | 2022-07-13 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Proven | 2021-09-25 | 2022-07-13 | Error is resolved
124 | fbc3947ff8c71b99b64b425d13903259d7cab6b9564d61ab45d9e513e20d50b7 | 2022-07-14 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Proven | 2022-07-07 | 2022-07-14 | Error is resolved
125 | e3a167cc0803bf7c5cf022ea605885a93473e126e24ec844b8e5effe0a866f75 | 2022-08-29 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Proven | 2022-08-23 | 2022-08-28 | Error is resolved
126 | 17f52913ab029b492307413649a45a03029ce92e2513a046fe6a8554f0a1a6db | 2022-08-30 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Proven | 2022-08-19 | 2022-08-30 | Error is resolved
127 | 8d7a1c27ba303114ee5da4a50880ea9bcd9296cc34b803fa508647059ec72f0d | 2022-09-21 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Proven | 2022-09-08 | 2022-09-21 | Error is resolved
128 | 86bc1f507bb909ee662c0b98adef8983a6841fd9a59ff605336154bd19eb7ee7 | 2022-11-02 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Proven | 2022-09-06 | 2022-11-12 | Error is resolved
129 | 40b2680e83eb0a70a09b7628cd63cc062fa46341b18a36ed04965c648047e488 | 2022-11-02 | Lack of pressure on secondary side (indirect connection) | Lack of pressure on secondary side (indirect connection) | 2 | 2 |  |  |  |  | Suspicion | 2022-10-04 | 2022-10-06 | Error is resolved
130 | fdd6811a47734fdeded36bade0439f8ed3398fa6bda0a7c0f951aeb6a48da522 | 2022-10-02 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Proven | 2022-10-06 | 2022-10-07 | Error is resolved
131 | 27ffd601d7392e4104b987c3584ef4e8bb5175341b8a87a9167bcbd01f87118f | 2023-01-10 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Proven | 2023-01-01 | 2023-01-05 | Error is resolved
132 | 0a6518ce349144c7113c4fade9bdc9f067abdf4d12011559469f329558d938a1 | 2023-01-10 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Suspicion | 2022-12-17
133 | 47db658ceea13d9b66dca4334b270741f0840be0d9863a2ad77662a005fe1704 | 2023-01-11 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Proven | 2023-01-06 | 2023-01-11 | Customer contacts VVS | /data/reports/71585514_20230124.pdf
134 | 7485cd9d71866d52e33b0de0f4cac2fe35dde09ee2cd5a72190fb74a86b8951c | 2022-06-14 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Suspicion | 2022-05-20 | 2022-06-14 | Error is resolved
135 | d639a11df73a92fa737467dcd27969642664fb33290d43221023843bc1ab0c48 | 2022-06-20 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Suspicion | 2022-06-14 | 2022-06-20 | Error is resolved
136 | bb149b3ef8aa1f742a3bc3a6868bb674164d63e4b211ae1e4b354f751bf721e5 | 2022-06-20 | User behaviour | User behaviour | 1 | 1 |  |  |  |  | Proven | 2022-04-27 | 2022-07-03 | No action
137 | 3342a1f65c1d6106401585f8dea5028c8a35770fc62e1aed8b11c55166dbccad | 2022-09-23 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Suspicion | 2022-09-22 | 2022-09-23 | Error is resolved
138 | 1c938320622143a9245e174421df9144ce60354585a1b4dc90fc94700e239a4d | 2022-11-01 | Pump failure | Pump failure | 1 | 1 |  |  |  |  | Proven | 2022-10-17 | 2022-10-28 | Error is resolved
139 | 4e9d5c5c8d893aa6a5455ff04dadecce0057ea034b2af8f102f2d737bb312e17 | 2022-10-31 | User behaviour | User behaviour | 1 | 1 |  |  |  |  | Proven | 2022-10-08 | 2022-11-01 | Error is resolved
140 | 23da1039f5f51a05ef9dac692d810e74f06fc3e8eacca5d177d1c435b2955b16 | 2022-10-31 | Radiator valve | Radiator valve | 1 | 1 |  |  |  |  | Suspicion | 2022-10-20 |  | Customer contacts VVS
141 | 39dc9dca35e6e9dfb9d6d4033fbdafd55e7ea4a9600fe79347a383a2f896cb9b | 2022-11-16 | Incorrect setting - Pump | Incorrect setting - Pump | 1 | 1 |  |  |  |  | Suspicion | 2022-11-03 | 2022-12-06 | Error is resolved
142 | b0a5aaad9ee686bcfc2239de26dffd508e2dbe6acb2cf8688c8b0789365bc04a | 2022-11-15 | Error in UFH master controller | Error in UFH master controller | 1 | 1 |  |  |  |  | Suspicion | 2022-04-13 | 2022-11-17 | Error is resolved
143 | 81cbc83f0334e149a298c459e7789f947b08c95304150e27f57e32023db11c99 | 2022-11-22 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Suspicion | 2022-11-15 | 2022-11-23
144 | 8e395c5149db3376a7eb630454130d7fce948926a02c63563605f3e0c6f6b6ac | 2022-11-23 | Too small heating surfaces | Too small heating surfaces | 1 | 1 |  |  |  |  | Proven | 2022-11-17 | 2022-11-24 | Error is resolved
145 | 125718702809f127968dd8d91ba431b3247eb7c7b3360c6f4eb1cecae3c6731b | 2022-11-23 | User behaviour | User behaviour | 1 | 1 |  |  | UFH incorrect setting | Incorrectly set underfloor heating. | Suspicion | 2022-11-27 | 2022-11-29 | Error is resolved
146 | a6f3b600c2153d88934c440c0bef1540bce14f571fe20b03712ca6eea0c94d01 | 2022-11-29 | User behaviour | User behaviour | 1 | 1 |  |  |  |  | Proven | 2022-11-17 | 2022-11-30 | Error is resolved
147 | 96a193a3618b146367a658e8be354293b35c4c111b1e6be134ac0a6521738371 | 2022-11-30 | User behaviour | User behaviour | 1 | 1 |  |  |  |  | Suspicion | 2022-11-26 | 2022-11-30 | Error is resolved
148 | 8dbbbff580463717ee524668f44955c9467865a4bf8c8eafae9b9515ea5e1c92 | 2022-11-30 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  | Radiator temp set too high | radiators set too high | Suspicion |  | 2022-12-01 | Error is resolved
149 | 8eaf61c3650caf2c73d51c08bb8913cf8dee0c4802e3df30927595acdbc2d718 | 2022-11-30 | UFH shunt | UFH shunt | 1 | 1 |  |  |  |  | Proven | 2022-06-29 | 2022-07-01 | Error is resolved
150 | 8eaf61c3650caf2c73d51c08bb8913cf8dee0c4802e3df30927595acdbc2d718 | 2022-12-09 | Incorrect setting - Pump | Incorrect setting - Pump | 1 | 1 |  |  |  |  | Suspicion | 2022-12-07 | 2022-12-10 | Error is resolved
151 | 7d7a0ca5634fe27d7b38c147618e942a6d947ff638b0ce455967c36cdb235930 | 2022-12-13 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Proven | 2022-12-11 | 2022-12-17 | Error is resolved
152 | 7d7a0ca5634fe27d7b38c147618e942a6d947ff638b0ce455967c36cdb235930 | 2023-01-16 | User behaviour | User behaviour | 1 | 1 |  |  | Wrong setting | Wrong setting | Suspicion | 2023-01-13 | 2023-01-17 | Error is resolved
153 | 91ca0af615c66ed729843e33a7f29266360fba09c75c15b6c4d95cab5c043f76 | 2022-12-15 | User behaviour | User behaviour | 2 | 1 |  |  | Thermostats set too high | Thermostats set too high | Suspicion | 2022-09-20 | 2022-12-17 | Error is resolved
154 | 384f3f2ef654304fe30553f95e35a273432e67738e3c19988b06059b3adfbe50 | 2022-12-15 | Radiator thermostat | Radiator thermostat | 1 | 1 |  |  |  |  | Suspicion | 2022-12-09 | 2022-12-21 | No action
155 | bf36b93a699423828c05fd3cea22bc30614df91bafde16966f48801f7222b303 | 2022-12-20 | User behaviour | User behaviour | 1 | 1 |  |  |  |  | Suspicion | 2022-10-14 |  | No action
156 | d161c21daac1fd182c9b70dcb5866576292dc972fdc84d4d7f3e1dc330dea4c1 | 2023-01-03 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 1 | 1 |  |  |  |  | Suspicion | 2023-01-01 | 2023-01-03 | Error is resolved
157 | 4c29d5870705f23d51e2a9bbb5a3f0ddbda43c745917076f17c5f6776d871b05 | 2023-01-04 | Other (SH) | Other (SH) | 1 | 1 |  |  | UFH unit fault | defective unit on floor heating | Suspicion | 2022-12-12 | 2023-01-05 | Customer contacts VVS
158 | d3f5c8598af860220999b06a43e8177563345afee013e6d330a9ca7cba26ae62 | 2023-01-05 | Radiator valve | Radiator valve | 2 | 1 |  |  |  |  | Proven | 2022-12-15 | 2023-01-14 | Error is resolved
159 | 286ed40c2419f5ad7a3f7cd34514c3eda3583dc21433f471dfac7390233a8f04 | 2023-01-05 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt. Bypass warm. | Suspicion | 2022-10-11 |  | No action
160 | 87fb4aa30cfff4191b0a2cb37ba4b7888b049f7f82c5fa5139e23c14d2f8de7a | 2023-01-17 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Proven | 2023-01-06 | 2023-01-18 | Error is resolved
161 | 49c3362ec8bf8618f173a5d0ad6ddec28c54751368eea52af491388088f2d407 | 2023-01-17 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  |  | Suspicion | 2022-11-26 | 2023-01-18 | Error is resolved
162 | 3978a2ce62cbf54ed9248fb63bd2a9037820c6df3c946df1a5fba36c8ea440dc | 2023-01-17 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  | Radiator temp set too high | Radiator set too high. User behaviour. | Suspicion | 2022-12-05 | 2023-01-18 | Customer contacts VVS
163 | fd6727ddd9edbb887409d3f0b9d121b1ab55239fb90f1a1ade95972f16fff3a6 | 2023-01-18 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  | Radiator temp set too high | Radiator set too high. User behaviour | Suspicion | 2023-01-16 | 2023-01-19 | Error is resolved
164 | b686b1e61946055a3b734f5a08a6fec0a9aa3bb39c5917ad99e0b42531ee3cc4 | 2023-01-20 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Suspicion | 2023-01-19 | 2023-01-21 | Customer contacts VVS
165 | e59e2f20b3b3cf154cf812130feb0624df584141a0bde24555d4d4a435bec1cc | 2022-05-17 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Proven | 2022-08-27 | 2022-05-18 | Error is resolved
166 | 2c75d5710ebd505a675bc4185899a721836b84f3cd1a383c22166527653fbe35 | 2022-05-18 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Proven | 2022-05-07 | 2022-05-19 | Error is resolved
167 | 976a3a9f44a2338db42570100cb93b22cfe935bef941516cf5a2f372002108f9 | 2022-05-19 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Suspicion | 2022-04-18 | 2022-05-20 | Error is resolved
168 | e2d8020b5a45f0f5c433e1342f1ee6a4dadf71ea8c5c37cc7a4bd6c4fbf4e438 | 2022-05-19 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt | Suspicion | 2022-05-13 | 2022-05-20 | Error is resolved
169 | d952db4e5f3e51612af12d70ed69367612bf8ea57aceea3df74beb6fed6f6aac | 2022-05-19 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | yellow heat shunt | Proven | 2022-04-18 | 2022-05-24 | Error is resolved
170 | 7eab2c6f021e17d1b3379bf47598a5e309ea692d9f6821c1fd8f2ad352a59247 | 2022-05-19 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Suspicion | 2022-05-24 | 2022-05-26 | Error is resolved
171 | bd67ee4d7b70a1c5326e5575eed6bbf8ab58097e02094c5d3e162675b6098a0e | 2022-05-19 | Telestat in UFH | Telestat in UFH | 2 | 1 |  |  |  |  | Proven |  | 2022-05-30 | Error is resolved
172 | 6e80db4f535a18b02e7b37220433a2ad85da7b2aa92008742c1b055db005a4ba | 2022-06-03 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Suspicion | 2022-05-28 | 2022-06-04 | Customer contacts VVS
173 | d6970f8832191645380c3b3708937a9d4d5019a2bb532e4e8db3bd6c523b61d5 | 2022-06-07 | Other (DHW) | Other (DHW) | 2 | 1 |  |  |  |  | Suspicion | 2022-04-15 | 2022-06-07 | Customer contacts VVS
174 | b31041dc2913e3b4af970c0b18f534c3d8ddec3888648055f7e41e459ffda0be | 2022-06-08 | Radiator valve | Radiator valve | 2 | 1 |  |  |  |  | Proven | 2022-06-05 | 2022-06-09 | Error is resolved
175 | 4d38c6d91871ce89935fc7d1ff03688146c52a65788243f3b43257bb623c7375 | 2022-06-08 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-06-09 | 2022-06-10 | Error is resolved
176 | 8bb3530b4075ef58869c9eec882721afe0dff8c56d02d283246d3e55b5bf5a1e | 2022-06-13 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 |  |  |  |  | Suspicion | 2022-05-11 | 2022-06-13 | Error is resolved
177 | 8419d47d4305176fb188fb355ecbb1c242290dc60bd48955fe1a1c24df243e70 | 2022-06-13 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Suspicion | 2022-05-19 | 2022-06-15 | Error is resolved
178 | fee351a16cd3a6d19519d7d43791ab33df383c3cc36fc4585baaeb4d8ef8444f | 2022-06-17 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt | Proven | 2022-02-16 | 2022-06-18 | Error is resolved
179 | db83ff71fc3fb8914e5c0d7d1c45e2cf447ccb43ab1f82df5e3d3d123c15778e | 2022-06-27 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2021-02-15 | 2022-06-28 | Error is resolved
180 | cfd8ae44e7c5026c4d054f79b1bd2ccc08aaa055089862a669f13d33c12209db | 2022-06-28 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 |  |  |  |  | Suspicion | 2022-06-26 | 2022-06-29 | Error is resolved
181 | 9e99c2e27616e24ea17e844e8a418b25830708d99ca4003884fc36ec2298dfd3 | 2022-06-28 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-05-23 | 2022-06-30 | Error is resolved
182 | 1dafa63c7d54a92a86f22f40942c270c087230a5645cb9d2c28a16011af65a9a | 2022-07-01 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  | Temp set too high | temperature set too high | Proven | 2022-02-03 | 2022-07-01 | Error is resolved
183 | 47310e7ed4b5c71ff9eb3a14573a15b2df7500d99304561e1ddc41b12fdcf7df | 2023-01-26 | User behaviour | User behaviour | 2 | 1 | 1 | 2 | UFH temp too low and radiator too high | Cooling. Review of facilities. Hot water regulated to 48 degrees. The convector radiators by the window were turned up high and the floor heating low around 18 degrees. Recommended to raise the floor heating and use it as primary heating and convector as secondary heating. Recommended to follow consumption on the watts app. Would like a new basket later. Addresses by email. | Proven |  |  |  | /data/reports/71587318_20230126.pdf
184 | ab88bbd5fd3c2ade43f05ee5816be4715ca678b67f196f51724707d647537e79 | 2022-07-04 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2021-04-15 | 2022-07-04 | Error is resolved
185 | 6e5b4c0ae1a7993b3b8411fbc11edc61848030b4dc919d4cca10b5505c6e19f7 | 2022-07-04 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Suspicion |  | 2022-07-05 | Customer contacts VVS
186 | 9f413d50153df096437630bc20d51f3c783a40ae005a86003e2a8046277ee123 | 2022-07-05 | Other (SH) | Other (SH) | 2 | 2 |  |  |  |  | Proven | 2022-06-10 | 2022-07-06 | Customer contacts VVS
187 | 7414e20a2c56abb115212f491612bd3dfceb25a73e897a9728c8e62e02f7dacf | 2022-07-05 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-04-13 | 2022-07-12 | Customer contacts VVS
188 | 90fea06072490044ad8b21e91e962bae20ffa9f5fb30197ccec7d08399c31f98 | 2022-07-06 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Proven |  | 2022-08-30
189 | 3d0ed82be1eade44db489e51333bccb06b9bc78af913ea5b0eef287777315ab4 | 2022-07-06 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 |  |  |  |  | Proven | 2022-04-24 | 2022-07-07 | Error is resolved
190 | f69c21301e41b9c0baa86bd8dda148acce3343bb35fa58ea09477cbb15e11e69 | 2022-07-06 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Suspicion |  | 2022-09-02 | Error is resolved
191 | bad8dd94b14d4f56974d977bc0caa4eb8c4517646590d270a908688d384bd907 | 2022-07-11 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 |  |  |  |  | Suspicion | 2022-06-25 | 2022-07-11 | Error is resolved
192 | 10b6d7d9e61a2041ed6b24f1db708aec1424ebe27e8a5adef3a2d4eb7d54bf5e | 2022-07-12 | Other (SH) | Other (SH) | 2 | 2 |  |  | Supply valve set too high | valve for flow too high (indirect) | Proven | 2022-05-18 | 2022-07-15
193 | a1c2f1a4a4c596ae2179f7e715f697a2a0febd071c7f8caa7a6e0ec5c290b73b | 2022-07-13 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | gold warning shunt - error set | Suspicion | 2022-07-10 | 2022-07-13 | Error is resolved
194 | ceea5c18757811d09b148af8ef528e256941775d08e1590f396ab5b5c756548c | 2022-07-13 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 |  |  |  |  | Proven | 2023-01-02 | 2023-01-17 | Error is resolved
195 | ceea5c18757811d09b148af8ef528e256941775d08e1590f396ab5b5c756548c | 2022-07-13 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  | Small radiator temp set too high | Small radiator screwed up well | Proven | 2023-01-03 | 2023-01-17 | Error is resolved
196 | 66ed2aa3a37f5a5dbea7950a3f46fd6a9fbac205e1e32d4b8adfe56e5e9ffa49 | 2022-06-01 | UFH shunt | UFH shunt | 2 | 1 |  |  |  |  | Proven | 2022-03-25 | 2022-05-31 | Error is resolved
197 | 4163de6eb6069e4929fc557c1549c3774608a3e1d3f2f5bea604d64f6f82973f | 2022-06-03 | Telestat in UFH | Telestat in UFH | 2 | 1 |  |  |  |  | Proven | 2022-05-01 | 2022-06-04 | Error is resolved
198 | 4163de6eb6069e4929fc557c1549c3774608a3e1d3f2f5bea604d64f6f82973f | 2023-01-26 | Telestat in UFH | Telestat in UFH | 2 | 1 |  |  |  |  | Suspicion | 2023-01-24 |  | No action
199 | 2029bbf43f028c8d85af601dc92f189b5925c6743332b47fc7b838ebed8a3d5f | 2022-06-07 | Other (DHW) | Other (DHW) | 2 | 1 |  |  |  |  | Suspicion | 2022-06-01 | 2022-07-06 | Customer contacts VVS
200 | 54ecb2cd91ba6488ad3b90c12528863a521420b9f81f3e0c163110eab07f1c2c | 2022-06-13 | Telestat in UFH | Telestat in UFH | 2 | 1 | [6 empty] | 2022-06-11 | Error is resolved
201 | 9bb4094ff8018be80a2191cd9d1646732abaac8edbb8cddbf1666d5c7ae352bb | 2022-06-13 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 |  |  |  |  | Proven | 2022-06-13 | 2022-06-14 | Error is resolved
202 | d6c68f64189d28ebe753fd1379634e79d0f76c585d2f7b43d7652a70ae5108f8 | 2022-06-13 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt | Suspicion | 2022-10-05 | 2022-06-18 | Error is resolved
203 | b7b26ecdb03dcb06e2676753a10c391ec5345892f8da253a1c7a191b3f4afc0f | 2022-06-17 | Towel dryer | Towel dryer | 2 | 1 |  |  |  |  | Proven | 2022-06-12 | 2022-06-17 | Error is resolved
204 | 3e16b8b732bd66b39e7e66f65ea928914451a06e72c49dd235ec11720f09baca | 2022-06-26 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt | Suspicion |  | 2022-06-26 | Customer contacts VVS
205 | 36c3ae28d6ca9dd46e7371edb88a6effbc6ca84cad1a959543f1a13fbd4b89a8 | 2022-06-22 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-05-14 | 2022-06-23 | Customer contacts VVS
206 | cc87e89e773559d83be40ea2199c69aa5780fae2d8f0bb8e01aaa95fafa6551b | 2022-06-22 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt | Proven | 2022-01-09 | 2022-08-16 | Error is resolved
207 | b84a7e72e8ef3e699b8b8440d718348ed026efd33d8d7cb39d6c00b4b1142b28 | 2022-06-22 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt | Proven | 2022-10-29 | 2022-06-24 | Customer contacts VVS
208 | 2d45ccd2d17c57f6f3596a1daef6ad59cd67fbf5d2fd2dd8b437c5dda9af7913 | 2022-06-24 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-06-24 | 2022-06-25 | Customer contacts VVS
209 | ce5910fdf67ad0b81cf410044173a3c1c6da9f2601920bcce14953740b34a2f4 | 2022-06-30 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 |  |  |  |  | Proven | 2022-05-20 | 2022-07-01 | Customer contacts VVS
210 | 8a781557d359ca7f8a12a6bc02cc0e39be05f9debfe0608875e2d9983a4d1ffe | 2022-07-01 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-06-30 | 2022-07-02 | Customer contacts VVS
211 | 463b49eedfdc23250632c26b30d59004122036b43b0a3a1e62e255a66949b2ad | 2022-07-06 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-07-01 | 2022-07-07 | Customer contacts VVS
212 | 4004cee5df006d08dd4e4260532cff9d78fb88ade28877e44880652377773ede | 2022-07-06 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 |  |  |  |  | Suspicion | 2022-04-18 | 2022-07-11 | Customer contacts VVS
213 | a4ff3babcfc8cd5b8b2586f14ed3ddcbbc1e1e67c1f6d38c314633b479070a86 | 2022-07-07 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt | Proven | 2022-04-17 | 2022-07-08 | Error is resolved
214 | a9a57ad594884b252949f46bf637118c95d5992826448b6b81b9ff9639daae6a | 2022-07-07 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 |  |  |  |  | Proven | 2022-01-20 | 2022-07-08 | Error is resolved
215 | e6fd1b6788cb5983581592c3ed37e52a3cc2b8506fdbca65e3f005c8d9c9faec | 2022-07-07 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt | Proven | 2022-04-15 | 2022-07-14 | Error is resolved
216 | 3ab8a197ac5c9da3b8b3847f72af1519ac9bb3f735ec128aa6638549b067cc87 | 2022-07-26 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-06-13 | 2022-08-30 | Customer contacts VVS
217 | edf191af6d3805c7c64358bead39f74689ed28f5512a15c56e2189ed15507307 | 2022-08-17 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Suspicion | 2022-03-31 | 2022-08-27 | Customer contacts VVS
218 | 28ce369bdca5ee98b9146094c7e1f269634a06bd7dbf3150eaded89f2ee88d54 | 2022-10-05 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 |  |  |  |  | Proven | 2022-09-29 | 2022-11-11 | No action
219 | f52e9ae831e93a68003a3dc75cd05666fbe3f1c549a3c7d09ebf85095f7a03b1 | 2022-10-10 | Telestat in UFH | Telestat in UFH | 2 | 1 |  |  | UFH fault | yellow heat ran wild | Suspicion | 2022-08-20 | 2022-10-02 | Error is resolved
220 | a382d00548596970b5730617a263383c1dbbb9d46db6bff8e386d74fbc94738e | 2022-10-18 | User behaviour | User behaviour | 2 | 1 |  |  |  |  | Suspicion | 2022-04-17 | 2022-10-10 | Error is resolved
221 | 88fa56254846da0c950e8d233e69531806e78b2d1daf45bce30ced62e98115d1 | 2022-10-18 | Error in UFH master controller | Error in UFH master controller | 2 | 1 |  |  |  |  | Suspicion | 2022-06-27 | 2022-08-29 | Customer contacts VVS
222 | 009aa72c5dd6dd537e124266b01bbec571f0f2dde6085d83e025fdeda9a3f735 | 2022-10-18 | UFH shunt | UFH shunt | 2 | 1 |  |  | UFH shunt fault | UFH shunt | Suspicion | 2022-10-08 | 2022-10-24 | Customer contacts VVS
223 | 09e7364e72dd3b6325998c2c2ea55607b498daa627d1219333596a66828ecd92 | 2022-10-18 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 |  |  |  |  | Proven | 2022-07-11 | 2022-10-28 | Error is resolved
224 | 7c221c47e664bee7d98452548e87715f743175334297bf80275a6fd250ca687e | 2022-11-03 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 |  |  |  |  | Proven | 2022-05-30 | 2022-11-03 | Error is resolved
225 | c54a7a8e227f73582d0557eb69540f9f55ef11020645de8ba4d155028ed881ae | 2022-11-03 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 |  |  |  |  | Suspicion | 2022-10-16 | 2022-11-09 | Customer contacts VVS
226 | 9f7e9a65637f2d841a037b8a8fbef1aae6b2d0eb4a534bf8688268a5f282a194 | 2023-01-26 | Other (SH) | Other (SH) | 2 | 1 | 2 | 3 | Storage tank pipe damage | Cooling. Nice cooling radiator/underfloor heating. The consumer said they had had a visit from the plumbing / pipe damage at the hot water tank. It has arisen in the context (time period) Consumer takes hold of plumbing. | Suspicion |  |  | Customer contacts VVS | /data/reports/71405651_20230127.pdf
227 | 0cee6c156283c23a70a4cb74ca7afdf2772ed0960c0ae9fb5b8dbc1f82fdf93d | 2023-01-10 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 1 | 1 | 1 | 1 | Motor valve for venting valve stuck in open position | Motor valve for VV stuck in open position. | Proven |  |  | Error is resolved | /data/reports/71582294_20230127.pdf
228 | 26ffa59c5435b0b5b7390c5f3b73b4da4b3216f4fb9cb9802b210a8fea804981 | 2023-01-30 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | DHW heat exchanger regulator fault | Large consumption (695 L/h) and poor cooling (delta T = 7 degrees). Possibly the domestic water regulator for the exchanger is the cause of poor cooling. When closing to the exchanger flow decreased to 130 L/h and cooling stabilized. Customer contacts VVS. | Suspicion |  |  | Customer contacts VVS | /data/reports/71162619_20230130.pdf
229 | bf1af8dd27fa2305d57a7f84b79d89edb53f234b4639a73dc020fa2bae5de84e | 2023-01-31 | Radiator valve | Radiator valve | 2 | 1 | 1 | 1 | Radiator without thermosat | Radiator in the living room without thermostat. The district heating meter must be moved to the main taps. Meter lacks sealing. Customer informed about having the meter moved and agreeing a time for sealing. | Proven |  |  |  | /data/reports/71828316_20230131.pdf
230 | 6a8052b300714db8c9e4724e6cafbb56092328282bdac11c345a000e0d999957 | 2023-01-31 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 | 1 | 2 | High water temp | Cooling. Housing association - suspicion of high water temperature. The heating engineer was contacted and informed about the lack of cooling. Will take care of it. | Suspicion |  |  |  | /data/reports/71757222_20230131.pdf
231 | 666b578f9b066b78f013b3c8559232fd456796f99881dce0c87d1e5cab801cb4 | 2023-01-31 | Other (SH) | UFH shunt | 2 | 1 | 1 | 2 | UFH shunt and valve controlling 2nd temp adjusted | Cooling. Older indirect plant. UFH shunt. Valve for controlling secondary temp. adjusted. Needs service. Informed about the service scheme and heat+. Have watts installed. Will contact VVS (possibly the service scheme) | Suspicion |  |  |  | /data/reports/71083411_20230131.pdf
232 | 6f4922ae9b22ddcd6f79d6831fb3fcddcc3009398c7f5a9410f4bab986cc8ebf | 2023-02-01 | Other (SH) | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | Heat exchanger valve fault | Valve for controlling the exchanger defective / loose. | Proven |  |  | Customer contacts VVS | /data/reports/71245445_20230201.pdf
233 | 6f4922ae9b22ddcd6f79d6831fb3fcddcc3009398c7f5a9410f4bab986cc8ebf | 2023-02-01 | Return thermostat set too high | Return thermostat set too high | 2 | 1 | 1 | 3 | Return valve in bathroom set down | Return valve bathroom adjusted down | Proven |  |  | Error is resolved | /data/reports/71245445_20230201.pdf
234 | f01b30c33b9f4ff333854a8cd07d1dbbf495cbb67a51c506ee9dba46b00308f6 | 2023-02-01 | User behaviour | User behaviour | 2 | 1 | 1 | 3 |  |  | Suspicion |  |  |  | /data/reports/71585260_20230201.pdf
235 | 5ed205ea3ca1f74df109622f6e3bd484ab5f7325f0581e829eabb6a1770942ac | 2023-02-01 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | UFH shunt set down still fault | Cooling. The customer said that the underfloor heating sometimes hissed. temp. in shunt very hot. Had consumer adjust valve down but it is not working properly. Recommended to have a plumber service it. The customer had watts installed and was registered for the service scheme. | Suspicion |  |  |  | /data/reports/71509550_20230201.pdf
236 | 97fa63b7893dd85b1d0dcfa3707d1715d2b77f1b9ee2bdbad0d7f5039292b948 | 2023-02-02 | Other (SH) | User behaviour | 2 | 1 | 1 | 1 | Radiator temp set too high | Cooling. Review of facilities. New alternator installed ok. It is estimated to be a radiator in the living room that was standing high. Recommended to open the radiator hides too much heat. Got customer to install watts on visit. | Proven |  |  | Error is resolved | /data/reports/71524437_20230202.pdf
237 | 43cb53dc9f98b63e573ebcdf54ebc6e304153f04fda8984d8be8670510901161 | 2023-02-02 | Towel dryer | Towel dryer | 2 | 1 | 1 | 1 | Towel dryer | Cooling. Review of facilities. It is estimated that the towel dryer in the bathroom is the cause of the lack of cooling. | Proven |  |  | Error is resolved | /data/reports/71241881_20230202.pdf
238 | e143e6dcc28785a1b0e33b2cd09913c2e47609476a54cb9756a7593d6bac11cf | 2023-02-06 | Other (SH) | User behaviour | 2 | 1 | 1 | 3 | Radiator temp set down | The radiator under the window section was very hot. This adjusted down. | Suspicion |  |  | Error is resolved | /data/reports/71405238_20230206.pdf
239 | ac740c9fd97269eb7881664b22f2338dbe958ec808965d94e8073ac07c5aae54 | 2023-02-07 | Other (SH) | Other (SH) | 2 | 1 | 1 | 2 | UFH master controller settings changed | ECL set for underfloor heating. Changed from comfort to auto by consumer. Review of installation. Follow-up later on whether changes have the desired effect. Sending mail | Suspicion |  |  | Error is resolved | /data/reports/60895056_20230207.pdf
240 | 3d6956a03ec0117ca80e77ec6f3402d285eaaf0529387e1252469b79da39b1c1 | 2023-02-07 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Radiator fault | Lack of cooling. Review of installation. It is estimated that a radiator at the entrance was the cause. Consumers show how the meter works. Recommended to get watts installed. | Proven |  |  | Error is resolved | /data/reports/71405883_20230207.pdf
241 | 066b62866f601657e114a41639ecb023da55b9186e89e869de97610cb9fab3c0 | 2023-02-08 | Too small heating surfaces | Too small heating surfaces | 2 | 1 | 1 | 3 | Radiator fault temp adjusted | Cooling. Review of facilities. It is estimated to be the radiator on the 1st floor under the window which is the cause of the lack of cooling. This adjusted and cooling increased. Review / explanation of the structure of the facility. Recommended to have watts installed to track consumption. | Proven |  |  | Error is resolved | /data/reports/71337889_20230208.pdf
242 | 217bfc66fe54884db33010e8969a51bb4401dcb714806fe8c0dbe0beb184a9b6 | 2023-02-08 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Mixed system on same shunt temp temp adjusted still fault | Cooling. Facility reviewed. Mixed underfloor heating and radiator. The fault is estimated to be underfloor heating and radiator running on the same shunt. temp. was adjusted up to 60 degrees to get heat in radiators. It is the same temperature that goes into the underfloor heating. Now when the underfloor heating does not call for heat and the pump switches off no heat comes to the radiator. Recommended to move supply to radiator circuit in front of shunt. Just signed up for the service scheme. Have watts installed. | Proven |  |  | Customer contacts VVS | /data/reports/71586584_20230208.pdf
243 | a807affb9cba171c4892c9dd296faf95548993877a631f283512cb9d6c31e2bb | 2023-02-08 | User behaviour | User behaviour | 2 | 1 | 1 | 1 | Using 2/3 radiators | Visit to customer regarding poor cooling. Kitchen-living room with 3 radiators one of which was closed. 2 smaller radiators in the room were set quite high (high consumption and insufficient cooling). This is probably the cause of poor cooling. Customer advised to use all radiators in the room and adjust thermostats accordingly. Meter and meter readings reviewed with customer. | Suspicion |  |  | Error is resolved | /data/reports/71162506_20230208.pdf
244 | dcb3ef30f405cd13759219fd0e32620d05ecb312c9f61c52db825b78983695a3 | 2023-02-09 | Other (SH) | User behaviour | 2 | 1 | 1 | 3 | UFH manual valve temp too high user set it slightly down | Visit to customer regarding poor cooling. 2 pcs. manual valves for underfloor heating in the bathroom and in the toilet probably cause insufficient cooling. Customer aware of problem but wants comfort with good heat in these rooms. Customer adjusts valves slightly for better cooling. Meter and meter readings reviewed with customer. | Suspicion |  |  |  | /data/reports/71163039_20230209.pdf
245 | 4f7540d83f54bee856386d8f18d6bf704319bacaa4d0f64ee6657b96d4815b07 | 2023-02-09 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 | 1 | 3 | Unknown | Cooling. Review of facilities. Cooling over heating circuit ok. AVTB exchange stood at just over three. The hot water controlled in the kitchen. The hot water was 12 l/h 70 degrees and 1800 l/h (T1 73)( T2 70) read on the meter. Printout of consumption provided. Will take father in plumbing. | Suspicion |  |  | Customer contacts VVS | /data/reports/71405193_20230209.pdf
246 | b912e979d5af91900fc79613c0fe91e594771c13a03ffec6748a2a0f7e31eefd | 2023-02-13 | User behaviour | User behaviour | 2 | 1 | 1 | 1 | Radiator temp set too high | Visit 10/2. Cooling. It is estimated to be a radiator in the room that was the cause. This adjusted down and better cooling. Recommended to get watts installed. Material on watts and service arrangement provided. | Proven |  |  | No action | /data/reports/71241381_20230213.pdf
247 | 4ce3e78a675061a0f0c8f7f9981b50571d55fcbbe527938cfe41ea5a9b464ca4 | 2023-02-13 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 2 | Unknown | Visit. Lack of cooling. 521 l/h Delta t 0.2 degree. Said he had a visit from the plumbing last week. The hot water was very hot. Will contact the plumbing. | Suspicion |  |  | Customer contacts VVS | /data/reports/60433540_20230213.pdf
248 | d7cb47874036b451ddcae2f90a75e199da2513b79afb2b6287f397c1cfecd2f9 | 2023-02-13 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Using small radiator in kitchen to heat living room | Visit regarding poor cooling. 2. smaller radiators in the kitchen-dining room tried to heat the kitchen-dining room and living room up!. Radiator in living room cold/closed and also covered by sofa. Customer advised to use all radiators in the rooms and set them the same. Good dialogue with the customer about heating surfaces heat utilization etc. Meter and meter readings reviewed with customer. | Suspicion |  |  |  | /data/reports/71626555_20230213.pdf
249 | 9d14855e064782634792ec392bfd08a2309b86aece8567e80ee92f2e55d4fe81 | 2023-02-13 | Other (SH) | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt fault | Cooling. Review of facilities. It is estimated to be a floor heating shunt in the basement under the ceiling that is the cause. This shut off and cooling improved. Customer handles plumbing. Would like to give a basket when the plumbing has made a mistake (Customer sends an email). Recommended to have watts app installed. | Suspicion |  |  | Customer contacts VVS | /data/reports/71525019_20230213.pdf
250 | 8f4165f8725a17f2c1d8f657d053abfa36de0fcf4dfddcfebe921753cc36a805 | 2023-02-14 | User behaviour | User behaviour | 2 | 1 |  |  | User shuts off heat during night | Cooling. The customer said that he turns off the heat in the living room at night and opens it again around 08.00. This causes the peak with lack of cooling. Recommended to keep an even temp. | Proven |  |  | Error is resolved | /data/reports/71585357_20230214.pdf
251 | d96ccd9595686276fae0f0d6dcc50a612a8a9a100b56478a1732487d780d5d76 | 2023-02-14 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 | 1 | 2 | Heat exchanger too high temp | Visit regarding poor cooling. (Flow = 92 L/h and Delta T = 5 degrees) When closing up to the hot water exchanger flow dropped to 0 L/h. High set temp. to the exchanger is considered to be the cause of poor cooling. The customer contacts their plumbing company for a review of the installation regarding leaky valve and adjustments. | Suspicion |  |  |  | /data/reports/71336490_20230214.pdf
252 | 208dbc0efd2e58f7bc507adc3e2461f6730f8455457286c9291efd4231e0c3c7 | 2023-02-15 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Valve fault wrong sensor placement | Cooling. Review of facilities. It is estimated to be valve sensor location for mixing circuit 1st string radiator. Feel element wrong and taped to pipe from shunt. Recommended to move the sensor so that it measures temp. in the circle. Customer handles plumbing. | Suspicion |  |  | Customer contacts VVS | /data/reports/71487936_20230215.pdf
253 | 5ee37c20cdcb35fcf510609666270e4eb28d9c965a8238045ddb1ec81477c8d8 | 2023-02-15 | Other (SH) | User behaviour | 2 | 1 | 1 | 3 | UFH manual valve temp too high | Cooling. Review of facilities. It is estimated to be manually regulated underfloor heating in the living room. Recommended to use this carefully and at the same time use a radiator to heat the living room. Recommended to get watts installed. | Proven |  |  | Error is resolved | /data/reports/71114844_20230215.pdf
254 | 04eb822ebf12397affe9070f7d06ea068435b3f9e09445245465222b9ead88df | 2023-02-15 | Other (SH) | Other (SH) | 2 | 1 |  | 1 | Smart thermostat lower temp settings | Visit. Has periods of lack of cooling. Review of facilities. The customer has smart thermostats with night lowering and they are also coded to shut down during the day to around 17 degrees. It is when the house calls for heating around 15.00 the problem occurs. Recommended to switch to valve with preset. Also recommended to replace older TD with a new one. Will contact you later to see if measures have the desired effect. | Suspicion |  |  | Customer contacts VVS | /data/reports/71085551_20230215.pdf
255 | da0eef0d3e5bcb6c4f8b92049c4a5ced30b6db26401905114d081148b5e03569 | 2023-02-20 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 |  | Heat exchanger AVTB valve fault | Cooling. It is estimated to be the valve AVTB for the exchanger which is the cause of the lack of cooling. | Proven |  |  | Customer contacts VVS | /data/reports/71256822_20230220.pdf
256 | 2cdc2a8a364000c53928681f4bc4d2bc9f38cab85e63a1d91089d04f335e62a9 | 2023-02-21 | Other (SH) | Other (SH) | 2 | 1 |  | 3 | Smart thermostat battery fault changed | Smart thermostat lacked power. New battery and ok cooling. | Proven |  |  | Error is resolved | /data/reports/71784921_20230221.pdf
257 | a15c19333d45f0762bec9adf199c43704176e85f1d4f47957b0000b7ae210e07 | 2023-02-21 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | Heat exchanger fault | Heat exchanger. | Proven |  |  |  | /data/reports/71509552_20230221.pdf
258 | ac22b1d37fab88407eb42b9253b00dc426b24767879e78d4f5747f3b370e410a | 2022-11-14 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 |  |  | DHW valve fault | Valve for controlling the hot water | Proven | 2022-11-12 | 2022-11-15 | Error is resolved
259 | 1dcb74933cc3b52a3612eae828dabfca7cc3818044af3e4cd91af6588211737f | 2022-11-17 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 1 | 1 |  |  |  |  | Proven | 2022-11-02 | 2022-11-18 | Error is resolved
260 | 98cf970ebb92b4dee6da2f8f17805c3a95a1e66feead259c2a30879cea260b94 | 2022-11-23 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 1 | 1 |  |  |  |  | Suspicion | 2022-12-22 | 2022-12-27 | Customer contacts VVS
261 | ba1b35ace226cb4f12690771bee03720fcd36a9bcfef0dc0b7478a7dca9a85ca | 2023-01-05 | User behaviour | User behaviour | 1 | 1 |  |  |  |  | Suspicion | 2022-12-13 | 2023-01-05 | No action
262 | 73f701d0e19598d445972284dce1bc8f513a380c8264fe4f13bbab966a76956f | 2023-01-05 | Incorrectly set weather compensation | Incorrectly set weather compensation | 1 | 1 |  |  |  |  | Proven |  | 2022-10-11 | Error is resolved
263 | 73f701d0e19598d445972284dce1bc8f513a380c8264fe4f13bbab966a76956f | 2023-01-05 | UFH shunt | UFH shunt | 1 | 1 |  |  |  |  | Proven |  | 2022-10-11 | Error is resolved
264 | f17569a233a802fb0d3b84bf2d58f7671946f17530a9aac4b55359d58be12ec8 | 2022-05-16 | Towel dryer | Towel dryer | 2 | 1 |  |  |  |  | Proven | 2022-05-05 | 2022-05-17 | Error is resolved
265 | b892d4ea5b3232ab5cfadc852709fb32334f9d7e50792c3e30b38b9d5167fde9 | 2022-05-17 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 |  |  |  |  | Suspicion | 2022-04-22 | 2022-04-17 | Error is resolved
266 | 57771b82ca10e30d77015859325701f715ebf67bce9f8f8edd719e86ba39ae94 | 2022-05-18 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2021-11-05 | 2022-05-18 | Error is resolved
267 | 60fc49e45351cc90fc7244b3fc2c8a4b7a8f599be7f5299b407c085e5ff29a49 | 2022-05-18 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 | [5 empty] | 2021-03-26 | 2022-05-19 | Error is resolved
268 | 0d41b1c4b6dc0920fa16070fc106a468cf6d67fc73ea621635aee89f7d906133 | 2022-05-18 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-03-25 | 2022-05-24 | Error is resolved
269 | 02214bb43b990d6a1b0186864f2e148e8600cc0047999f0e7b67641801da7ca8 | 2023-02-23 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Poor cooling: direct connection to UFH without a shunt | Cooling. Review of facilities. The customer had a new underfloor heating control installed on 15/2 before he regulated it manually. The underfloor heating distribution pipe is connected directly to the district heating without a floor heating shunt in front. This is considered to be the cause of the lack of cooling. Customer contacts VVS. Graph of temperature and consumption sent by email. | Suspicion |  |  | Customer contacts VVS | /data/reports/71406752_20230223.pdf
270 | daf8009af4abfda95b3e04a8126cc7e5f434af3e5c6ed24ccc0410f28c87428a | 2023-02-23 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Old pressure differential and radiator valve UFH temp set down | Cooling. Review of facilities. In periods of lack of cooling. Customer experiences the hissing in the radiator. Old pressure diff. and radiator valve without preset. Underfloor heating in bathroom adjusted down. Recommended new TD and valves with preset. | Suspicion |  |  | Customer contacts VVS | /data/reports/71792069_20230223.pdf
271 | 1fcc14bcdab100eb40cb5bcd529f763c90da1af01f14ce8933de2b8af2983e38 | 2023-02-24 | User behaviour | User behaviour | 2 | 1 |  |  | Using few radiators instead of all of them evenly | Cooling. Uses few radiators for heating. Recommended to maintain an even heat. (English speaking resident) | Proven |  |  |  | /data/reports/71337216_20230224.pdf
272 | bc2faef6aa593eb74750912f8318ec8bb54d1a672768908083d9506bb12dd4f2 | 2023-02-24 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 1 | 1 | 1 | 1 | Defective alternator | The alternator is defective - will be replaced on Monday 27/2 | Proven |  |  | Customer contacts VVS | /data/reports/71539638_20230224.pdf
273 | 7ce9363f75307957d9617c6316609e7524f94616baec205b44ec62546811e059 | 2023-02-24 | Other (SH) | User behaviour | 2 | 1 | 1 | 3 | Radiator temperature adjusted to lower | Visit to customer regarding poor cooling. 1-string system. The customer adjusted the temp. to the radiators. Flow decreased and cooling slowly improved. Follow-up of adjustments and contact with customer next week. | Suspicion |  |  |  | /data/reports/71112899_20230224.pdf
274 | 2f19241c00ea67cc338fe19dd39dd0b89f7d03623d50e00dbc108dcb52369845 | 2023-02-24 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 1 | 1 | 1 | 3 | Heat exchanger valve fault | Valve on exchanger defective | Proven |  |  | Customer contacts VVS | /data/reports/71523721_20230224.pdf
275 | 310dbc66640664d64fb21b7e03eeaa15c7255cef530a6f12c5c33487ba0b87c3 | 2023-02-27 | Other (SH) | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt fault | Cooling. Review of facilities. Radiator 1st floor ok. Alternates ok. Underfloor heating living room / basement. It is estimated that the UFH shunt is the cause of the lack of cooling. Recommended to have the shunt reviewed at VVS. Recommended to get control of shunt (telestat / master and room sensor) Watts and meter data reviewed. | Suspicion |  |  | Customer contacts VVS | /data/reports/71784980_20230227.pdf
276 | 5ad9864f451e019dc982a128cba6421523ca40a29ada6ef2e11b85aea5e8487c | 2023-02-27 | UFH shunt | UFH shunt | 2 | 1 | 1 | 2 | Shunt fault | Visit regarding fluctuating/high consumption and therefore poor cooling. Suspicion of shunt as the cause of poor cooling. Customer contacts VVS for review of installation. Meter and meter readings reviewed with customer. | Suspicion |  |  | Customer contacts VVS | /data/reports/71114251_20230227.pdf
277 | 035d0290c9bdcfb1ac8543ac19a13f47a35b98beea9db0451a5ec262d6e13d48 | 2023-02-27 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 1 | 1 | 1 | 1 | DHW: stuck motor valve in open position | Hot water motor valve stuck in open position | Proven |  |  | Error is resolved | /data/reports/78221576_20230227.pdf
278 | 0178f38f9af08376e5fc03d1eac27fa603463e37d2ac09373fa2d8bc66a1b1db | 2023-03-03 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Small radiator in kitchen temp too high | Visit regarding increasing consumption as well as poor cooling. Smaller radiator in kitchen was fully open with insufficient cooling as a result. By adjusting this radiator flow dropped considerably and cooling slowly stabilized. General heating advice discussed with customer. Meter and meter readings reviewed with customer. | Suspicion |  |  |  | /data/reports/60985150_20230303.pdf
279 | e05ede73ac198c20393b936ad37c80386b21e1262cfec168c9ef38a06253b575 | 2023-03-03 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | High set temp for DHW heat exchangers | Visit regarding poor cooling. House not inhabited. High set temp. for hot water exchangers is considered to be the cause of high consumption as well as poor cooling. Customer adjusted temp. to changers and flow dropped considerably. Cooling is expected to stabilize after adjustment. Meter readings reviewed with customer. | Suspicion |  |  |  | /data/reports/71241482_20230303.pdf
280 | 72ec26c4192de47fb7500d6413aae47ce9cb94f5c9dba7200e27a214e6def4dc | 2022-05-25 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 |  |  |  |  | Proven | 2022-04-20 | 2022-05-25 | Error is resolved
281 | b711b3dcbd471208bc725a68b83a9f137eefa75f08baa1ba8aca2aeebb32be38 | 2023-03-03 | Return thermostat set too high | Return thermostat set too high | 2 | 1 | 1 | 3 | Return valve fault in the bathroom | Cooling. Review of facilities. Delta t 10. It is estimated that the return valve in the bathroom is the cause of the lack of cooling. This adjusted down and immediately good cooling. Recommended to get watts installed. | Proven |  |  | Error is resolved | /data/reports/71635364_20230303.pdf
282 | be8d5e7e47ddda6563e5da5654b9307375eed8ffb0e8bcd69b20189ea9c4d206 | 2023-03-06 | User behaviour | User behaviour | 2 | 1 | 2 | 3 | User behaviour: setting radiator high and low | Visit regarding increasing consumption as well as poor cooling. User behaviour is considered to be the cause of poor cooling. The customer opens and closes a smaller radiator in the living room and hallway as needed with inadequate cooling as a result. General heating advice discussed with customer. Meter and meter readings reviewed with customer. | Suspicion |  |  |  | /data/reports/71585788_20230306.pdf
283 | a15c19333d45f0762bec9adf199c43704176e85f1d4f47957b0000b7ae210e07 | 2023-03-07 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Master controller adjusted to radiator radiator temp set down | Cooling. Review of facilities. ECL adjusted to radiator. (temp. stood at 5) Radiator 1st floor adjusted down. (presetting) Recommended to create free space in front of the radiator. Recommended to get watts installed. Would like to have new graph sent later. | Suspicion |  |  | Error is resolved | /data/reports/71509552_20230307.pdf
284 | 63ecb4d9e0b5885490debb635ef6ad20f4e7957bf1ee77204b0ce7c92422f66b | 2023-03-07 | Other (SH) | Other (SH) | 2 | 1 | 2 | 3 | Cooling issue: Heating fan fault | Cooling. Review of installation. It is estimated that the heater in the workshop is the cause of the lack of cooling. Will tackle plumbing. | Proven |  |  | Customer contacts VVS | /data/reports/71085397_20230307.pdf
285 | 7e6cc415fe5dca185a95786dfa57a9f45780acb1681f864f8ea364e5fadecd28 | 2023-03-07 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 |  |  | Test | test on March 7 | Suspicion | 2023-03-01 | 2023-03-10 | Customer contacts VVS | /data/reports/71083493_20230307.pdf
286 | 1e3f8c79d80aaa054b6bcd76abf6ee61a4b27024f50116f35423f72e48107a2b | 2023-03-08 | Other (SH) | Other (SH) | 2 | 1 |  |  | Cooling issue: Heating fan not connected to power supply | Cooling. House under renovation and a caloifere has been connected but the power had been taken from it and no cooling. | Proven |  |  | Error is resolved | /data/reports/71374077_20230308.pdf
287 | faf0c99f07c42ef6f545a2a595bff9668587f8c7034aa6ba6cf7f835829a6ac4 | 2023-03-08 | Radiator thermostat | Radiator thermostat | 2 | 1 | 1 | 1 | Small radiator in kitchen temp too high | Cooling. It is estimated to be a small radiator in the kitchen that was turned up too high. | Proven |  |  | Error is resolved | /data/reports/71163135_20230308.pdf
288 | 7e6cc415fe5dca185a95786dfa57a9f45780acb1681f864f8ea364e5fadecd28 | 2023-03-08 | Radiator thermostat | Radiator thermostat | 2 | 1 |  |  |  | asjd asd jasdnasjdnasjdn as dn |  |  |  |  | /data/reports/71083493_20230308.pdf
289 | 825441b7ab7dc663a122547371fc18368c3ae3a0bc9c7c85d5564f968d7833da | 2023-03-08 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Possible: high set radiator valves radiators covered thermostat fault UFH sensor misplacement | Visit regarding high consumption and poor cooling. Installation difficult to access due to shelves/furniture. Several possible causes of poor cooling. : High set radiator valves - Radiator covered by sofa. - Radiators enclosed in hiders. - Possible faulty radiator thermostat. - Room sensor for underfloor heating (guest toilet) is in the kitchen drawer. The customer contacts their plumber for a review of the installation. General heating advice provided/discussed with customer. | Suspicion |  |  | Customer contacts VVS | /data/reports/61629896_20230308.pdf
290 | b9e2476a13502270a6aec1b2977c0f35471b18bfffd272c39710b7061004bfac | 2023-03-09 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 1 | 1 | 1 | 1 |  | Contacted Tanja from AB Himmerland | Proven | 2023-03-07 | 2023-03-09 | Error is resolved | /data/reports/69690838_20230309.pdf
291 | e015c14bc53ea455d3ed727a63f5b8bbd29365416174d9b294a59c884349dad5 | 2023-03-09 | Other (SH) | UFH shunt | 2 | 1 | 1 | 2 | UFH check-valve fault | Cooling. l/h 70 delta h 4 degrees. Alternates ok. Underfloor heating is considered to be the cause of the lack of cooling. (contra - valve) Will contact owner-occupied housing administration to get a plumbing. | Suspicion |  |  | Customer contacts VVS | /data/reports/71406936_20230309.pdf
292 | 514d4b01c1925d0112936f6f297c4bc0bc32b64df68e60d82dd0be5de2e4777d | 2023-03-10 | Other (SH) | User behaviour | 2 | 1 | 1 | 3 | Radiator valve temp too high | Cooling. It is estimated to be the radiator in the bedroom that was turned up. | Proven |  |  | Error is resolved | /data/reports/71587359_20230310.pdf
293 | a8b99dcf3de3fcaa514e417fe7f2c000e19cdd59deeffdf1204afef7dc734286 | 2023-03-14 | Other (SH) | User behaviour | 2 | 1 | 1 | 3 | Radiator valve set down | Visit lack of cooling. The customer said that he had turned down the radiator just before the visit and this is considered to be the cause of the lack of cooling. The customer will now be visited by the service scheme on Friday 14/3 - 23 | Suspicion |  |  |  | /data/reports/71749187_20230314.pdf
294 | 1e662755a21cc595d28ec27d1038f54d7cf9e14a1a129ddb408aabe75c897afa | 2023-03-14 | UFH shunt | UFH shunt | 2 | 1 | 1 | 2 | UFH shunt fault | Visit to customer regarding fluctuating consumption as well as poor cooling. It is estimated that the shunt to the underfloor heating system may be the cause of poor cooling. Customer contacts own plumbing. Meter and meter readings reviewed with customer. | Suspicion |  |  | Customer contacts VVS | /data/reports/60696738_20230314.pdf
295 | cb27487a5265883fcb50a0e678b26e5a1b7eb2ff16e20277a825df155c12a20e | 2023-03-15 | Other (SH) | UFH shunt | 2 | 1 | 1 | 2 | UFH shunt fault | Cooling. Review of facilities. It is estimated that the UFH shunt is the cause of the lack of cooling. temp. in shunt was very hot even though thermostat on temp. in the mixing circuit was set low. Recommended to get plumbing and service on shunt. Customer applies for a new basket when rep. is carried out. | Suspicion |  |  | Customer contacts VVS | /data/reports/71336738_20230315.pdf
296 | ec24c5d600e9e81845cdb050469d059d75711f1f560604ddc7ca7c582542458e | 2023-03-17 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 1 | AVTB valve (controlling DHW temperature?) set down | Cooling. Review of facilities. 93 l/h delta h 1.5. It is estimated to be AVTB for controlling the hot water which is the cause of the lack of cooling. Radiators good cooling. Recommended to get watts installed. | Suspicion |  |  |  | /data/reports/71245269_20230317.pdf
297 | d7808790b404c2b647a1494d8183a4d0164ce9bd362919e297dcfeada4b63ef3 | 2023-03-20 | Pressure differential regulator | Pressure differential regulator | 2 | 1 | 1 | 3 | Pressure differential regulator fault | Review of plant - Lack of cooling in periods. Older TD may be the cause. The customer guided in plant construction and what they should look out for in order to troubleshoot the plant. Basket delivered to customer and recommended to have watts installed. Will contact you later. | Suspicion |  |  |  | /data/reports/71792031_20230320.pdf
298 | 9655eef8337ba8fd7850cfcbdbfed16b0a6c10c9bf3e3469c977d4c59b59ecaa | 2023-03-20 | Other (SH) | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt fault | Cooling. The customer said that the plumbing was requisitioned and he was aware of the lack of cooling. Review of facilities. It is estimated that the UFH shunt is the cause of the lack of cooling. | Suspicion |  |  | Customer contacts VVS | /data/reports/71750351_20230320.pdf
299 | 2af5f72650d2a06dc9224d31f2864e4bc007057374e3f3f98da95a72215aad5d | 2023-03-24 | Other (SH) | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt fault | Cooling. Review of installation. House under renovation. Radiator and alternator ok. It is estimated that the shunt on the 1st floor is the cause of the lack of cooling. Lack of cooling has arisen in connection with the plumbing having shut off water on the hoses (14/2 09.00). Customer will deal with plumbing immediately. Recommended to get watts installed. The customer will contact you later to have a new basket sent. |  |  |  | Customer contacts VVS | /data/reports/71076735_20230324.pdf
300 | 197e53fd872246b8b8373cf0c07422c051b01730ccaa1683f55b373712aac4a9 | 2023-03-24 | Other (SH) | UFH shunt | 2 | 1 | 1 | 2 | UFH shunt fault | Visit lack of cooling. Review of facilities. It is estimated that the UFH shunt is the cause of the lack of cooling. The sensor element for adjusting the temperature in the shunt was changed at some point. But the new sensor is stripped firmly on the side of the shunt and not like the old one (mounted in the water stream). Recommended to get felt moved. Is registered for the service scheme and will contact VVS. | Suspicion |  |  | Customer contacts VVS | /data/reports/71524066_20230324.pdf
301 | a3fdaaf521a5c127dc90d0ef940e6a73a9d4460ee8efd19177793c8d1d3fe751 | 2023-03-27 | Other (SH) | Incorrectly set DHW temperature - heat exchanger | 2 | 1 | 1 | 3 | DHW temp set down | Cooling - Review of facilities. Hot water temp. was very high. Adjusted to 50 degrees by customer (2 on regulator) ECL 110 adjusted to radiator. Heat curve 1.0 min temp. 30 degrees. max flow 65 degrees. temperature 21 mode AUTO. by customer. The customer would like to have a new curve later to see if measures have had the desired effect. | Suspicion |  |  | Error is resolved | /data/reports/71113508_20230327.pdf
302 | bedd08e59d1ca0367bca02a07d107486ee9a96ab30ef9f7b137edd27694b7a87 | 2023-03-29 | Other (SH) | Other (SH) | 2 | 1 | 1 | 2 | UFH shunt sensor fault | Cooling. Review of facilities. New exchanger and underfloor heating. The sensor for the UFH shunt had fallen out of the pocket. This set in place. This is considered to be the cause of a lack of cooling. | Proven |  |  | Error is resolved | /data/reports/71587379_20230329.pdf
303 | 156f12ab91008f44dbcd8de4b834ba9c26891f09a2c9f0922a0e516d6eb5fb8b | 2023-03-31 | Other (SH) | Incorrectly set DHW temperature - storage tank | 2 | 1 | 2 | 3 | DHW temp set down | Visit due to lack of cooling. Hot water temp. adjusted down. Customer recommended 55 degrees VVB. Smart thermostats customers will switch to general. Customer examines whether valves are pre-set. Measure data reviewed with customer and general heating advice. Would like a new graph sent when he has had the plumbing over. | Proven |  |  | Customer contacts VVS | /data/reports/71246066_20230331.pdf
304 | 202038bea1aeb31307622b200fd2b01c733f9810d1cada9bf2cd338b4936a61d | 2023-04-03 | Other (SH) | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt/check-valve fault possible heat exchanger fault | Visit due to lack of cooling and high consumption. Review of installation. It is estimated that the UFH shunt is the cause of the lack of cooling. This shut off and consumption normally. The customer will contact VVS for a review of the system. The customer said that there was not much pressure on the hot water. Exchanger is an older termix 20 from around 1988. Recommended to get plumbing to look at it but it is due for replacement. Informed about the possibility of heat+. | Proven |  |  | Customer contacts VVS | /data/reports/71487556_20230403.pdf
305 | 8578832fc0cd84383e5aa3facca1e849efc9cb110476316d18ff1026e62ec962 | 2023-04-03 | Other (SH) | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt/check-valve fault in bathroom | Visit due to lack of cooling and high consumption. House under renovation. Review of facilities. It is estimated to be an UFH shunt in the bathroom (Wavin) Possibly a non-return valve. Customer handles plumbing. Print of temp. and flow delivered. | Proven |  |  | Customer contacts VVS | /data/reports/71509139_20230403.pdf
306 | 07ff1d6467f9e1912775c8c3769b741e600cc267b49f14e9210cd8bbe68748e6 | 2023-04-04 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Cooling issue | Visit due to lack of cooling (peak) After the first inquiry the cooling looks better. The customer has got a new exchanger and has smart thermostats. Recommended to try to avoid night lowering for a period of time. Will contact you for a new curve later. | Suspicion |  |  | No action | /data/reports/71241623_20230404.pdf
307 | e03d5dd8cdb0dcbff3b6e7ec1ec24994198d4453c3c6bbb7549f0d2b394ce31b | 2023-04-04 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 1 | 1 | 1 | 1 |  | Replacement of bill of exchange - old bill of exchange was 5 years old | Proven | 2023-03-28 | 2023-04-11 | Error is resolved | /data/reports/69108339_20230412.pdf
308 | 3bbee72df25d2914d6c61096a707e041182e552ffd9a5aad45878a0287ccc36a | 2023-04-12 | Radiator valve | Radiator valve | 2 | 1 | 1 | 3 | Radiator valve set down | Visit regarding increasing consumption and therefore poor cooling. High set radiator valve in basement (position 5) cause of high consumption. Customer adjusted valve and flow dropped from 348 L/h to 75 L/h. Cooling and heat utilization are expected to stabilise. Meter and meter readings reviewed with customer. | Proven |  |  | Error is resolved | /data/reports/71114711_20230412.pdf
309 | 70d4260cecee6086a579e114e319b8807c535d760d40d03023c140d68547816f | 2023-04-12 | Other (DHW) | Other (DHW) | 2 | 1 | 1 | 3 | Alternator fault | Cooling. Is on the service scheme and had the valve replaced on the exchanger in February. It is considered to be an alternator fault. This shut off and consumption dropped significantly and nice cooling. Recommended to get watts installed on phone. | Suspicion |  |  | No action | /data/reports/71337833_20230412.pdf
310 | 6475857a0bfa54d2861b7cbe04aeb07d9cc0a59e9439d18200ecd28bfe4f635c | 2023-04-12 | Other (SH) | Radiator valve | 2 | 1 | 1 | 3 | Radiator fault | Visit due to lack of cooling. The customer said that she had shut down the heating on 8/4. Nice cooling during review. It is estimated to be a small convector radiator in front of the window that may be a cause of the lack of cooling. Recommended to get watts installed. General heating advice discussed. | Suspicion |  |  | Error is resolved | /data/reports/71487955_20230412.pdf
311 | 07e2ac924deda0ec26874ab4141721b5c20041344bcc8d3bab00109ff07a41f7 | 2023-04-13 | Other (SH) | Other (SH) | 2 | 1 | 1 | 2 | Weather compensation valve fault | Visit due to lack of cooling and high consumption. It is estimated to be the engine valve for weather compensation that is defective. Customer contacts VVS. | Suspicion |  |  | Customer contacts VVS | /data/reports/60433485_20230413.pdf
312 | f9e6fa384ac0d3af23f72c90fb9a936e3f2bc61c5c936c2eba7e68c73809ac74 | 2023-04-17 | Other (SH) | Other (SH) | 2 | 1 | 1 | 1 | Secondary side temp set down | Visit due to lack of cooling and high consumption. Review of facilities. Indirect plants where supply temp. secondary side was turned up high. This adjusted. Genbo will help with settings in the future. Considering the service scheme. | Proven |  |  | Error is resolved | /data/reports/71335751_20230417.pdf
313 | ade58343dd02d9a0bdbf5f01e260871ed1f4661ae774f5cbb0c12fe487c3c78c | 2023-04-17 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 | 2 | 1 | Storage tank temp too high | VVB temp. set high. Recommended to adjust to 55 degrees. Material about the service scheme and heating + delivered | Proven |  |  | Error is resolved | /data/reports/71749089_20230417.pdf
314 | fdd6811a47734fdeded36bade0439f8ed3398fa6bda0a7c0f951aeb6a48da522 | 2023-04-19 | Other (SH) | Other (SH) | 2 | 1 | 2 | 3 |  | Visit due to lack of cooling. Review of facilities. | Suspicion |  |  | No action | /data/reports/71585562_20230419.pdf
315 | e25eb668509f213b377c1beb68108a5c6e1df79baa267eaa27204ad767407d43 | 2023-04-21 | Other (SH) | Other (SH) | 2 | 2 | 2 | 3 | Secondary side flow set down | Visit due to lack of cooling. Review of facilities. Indirect plant. Recommended to adjust the flow secondary side down. Consumption fell after adjustment from 125 l/h to 3 l/h. General talk about heat utilization. Informed about the possibility of heating + and material about the service arrangement and Watts app. | Suspicion |  |  | No action | /data/reports/71256664_20230421.pdf
316 | 1a28da51bbb1470d8ff93ad6f1e995700ff8e27424fd27bc745dd27ef9428c80 | 2023-04-24 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | Heat exchanger fault | Visit regarding poor cooling. It is considered to be defective in the hot water exchanger which is the cause of poor cooling. Good cooling from heating system. The customer contacts VVS to rectify the fault. Meter readings reviewed with customer. | Suspicion |  |  | Customer contacts VVS | /data/reports/71509937_20230424.pdf
317 | 1a4d324973e73c0eacb976c8ee8f7090f5388d379e84d8a861476477a2415620 | 2023-04-25 | Other (SH) | UFH shunt | 2 | 1 | 1 |  | UFH shunt/check-valve fault | Visit due to lack of cooling. Review of facilities. 75 l/h delta t 6. It is estimated that underfloor heating is the cause of the lack of cooling. Check valve / Valve. The customer contacts the chairman of the owner's association. | Suspicion |  |  | Customer contacts VVS | /data/reports/71524058_20230425.pdf
318 | 105a7b0579a0069b25bd6ba04ab02b646e16996818fb508dca4e36881847ece3 | 2023-04-26 | Temperature regulator - storage tank | Temperature regulator - storage tank | 2 | 1 | 1 | 2 | Heat exchanger fault | Lack of cooling of district heating and high consumption. Review of facilities. cooling heating circuit ok. It is considered to be an alternator fault. 500 l/h delta t 4. Recommended to get hold of plumbing as soon as possible. | Suspicion |  |  | Customer contacts VVS | /data/reports/71587020_20230426.pdf
319 | 9b256871a60a91e4cd0a1cd5739b841c28c5c7d025d9078361b068b89437954b | 2023-04-26 | Other (DHW) | Other (DHW) | 2 | 1 | 1 | 3 | Possible shower tap fault | Visit due to lack of cooling. Review of facilities. The customer said that he had turned up the hot water because he didn't think it was hot enough in the shower. It could be a faulty shower battery. Recommended to install watts to follow consumption/heat utilization. | Proven |  |  | Error is resolved | /data/reports/71524190_20230426.pdf
320 | 747446a4092348a7ae5a6a0548747e9b6de94bd53a44722880ffc4471f201336 | 2023-05-03 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 1 | DHW heat exchanger temp fault | It is estimated to be the domestic water regulator for the heat exchanger which is the cause of fluctuating consumption and insufficient cooling. (one-string plant). Customer contacts VVS. Customer informed about Watts and leaflets regarding service arrangement delivered. | Suspicion |  |  | Customer contacts VVS | /data/reports/71337641_20230503.pdf
321 | c4c3bfb859012b98d4339f2f396f053167f455b3bb8580db5ab632ac4309ac2f | 2023-05-08 | Other (SH) | Other (SH) | 2 | 2 | 1 | 1 | Indirect system leaking | Visit due to lack of cooling. Older indirect system (leaking in several places) It is estimated to be the flow secondary side that was turned up too high. Brochure on heat+ and the service scheme delivered. Recommended to adjust flow spring - summer - winter. | Suspicion |  |  | Customer contacts VVS | /data/reports/71338167_20230508.pdf
322 | 8fa8525c52fbae5a3c61d9b1841e2a08eff777e80878cbf920608889b038ebaf | 2023-05-09 | Other (SH) | UFH shunt | 2 | 1 | 1 | 2 | UFH shunt/check-valve fault | Visit due to high consumption and lack of cooling. 200 l/h delta t 0.8g. Review of the system - It is assessed that the UFH shunt is the cause of the lack of cooling. Possibly counter valve -valve. Recommended to get plumbing is to go through installation. Will come back later for new graph. | Suspicion |  |  | Customer contacts VVS | /data/reports/71405279_20230509.pdf
323 | d2e27c0334845f318e66cac353d033f1a054ba7f85e8adaa457709928357b1e4 | 2023-05-10 | Other (SH) | Other (SH) | 2 | 1 | 2 | 3 | UFH manual valve set down | Visit regarding poor cooling. Delta-T = 12 degrees. It is assessed to be the 2nd paragraph. manual valves for underfloor heating in the guest toilet and bathroom which cause poor cooling. When closing the manual valves flow decreased from 90 L/h to 21 L/h. Cooling is expected to stabilize afterwards. Meter readings reviewed with customer. General heating advice discussed with customer. | Suspicion |  |  |  | /data/reports/71242120_20230510.pdf
324 | 85b2f49e607dd60c65f8d595005b527c0be8c52a4d386437aac6dec16b05b6b6 | 2023-05-10 | UFH shunt | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt temp adjusted | Visit regarding poor cooling. Flow = 130 L/h and delta-T = 12 degrees. Customer has exercised/adjusted temp. regulator for UFH shunt and flow dropped to 36 L/h. Delta-T then = 35 degrees. The customer monitors consumption and cooling going forward for possible defect in shunt/check valve. | Suspicion |  |  |  | /data/reports/71246051_20230510.pdf
325 | 1f7dbcc3e97ec8658f325bf9aab670fed349a96850c523d5761b6b33c9e41e56 | 2023-05-11 | Radiator thermostat | Radiator thermostat | 2 | 1 | 1 | 3 | Radiator thermostat fault | Visit regarding fluctuating consumption as well as poor cooling. Review of facilities. On arrival at the customer normal consumption and fine cooling. Meter and meter readings reviewed with customer. Possibly a faulty radiator thermostat causing the problem. The customer changes the thermostat and the customer's consumption and cooling are followed up next week. | Suspicion |  |  |  | /data/reports/71406273_20230511.pdf
326 | e984818778796f1c19688c2ba3d7fc19d40014f73b21e702df9ab9eb99b79308 | 2023-05-11 | Other (SH) | UFH shunt | 2 | 1 | 1 | 2 | Shunt/check-valve fault | Visit lack of cooling. Review of facilities. DHW circulation recommended time-controlled. Return from shunt very hot. Possibly shunt valve counter. Customer will try to move the sensor to shunt temperature. Recommended to install watts. Will contact you later | Suspicion |  |  | Customer contacts VVS | /data/reports/71337770_20230511.pdf
327 | c386f64ef9b63c9c334e627bc413be3f1c1425bfedbff9c9d43ccef399c8a721 | 2023-05-12 | Incorrectly set DHW temperature - storage tank | Incorrectly set DHW temperature - storage tank | 2 | 1 | 2 | 3 | DHW too high temp | Visit regarding poor cooling. Flow = 130 L/h and delta-T = 15 degrees. The customer is registered for the service scheme and has d.d. contacted VVS regarding letter from the supply about insufficient cooling. Visit by VVS start February regarding service arrangement. Possibly high set temp. for domestic hot water cause poor cooling. Domestic hot water measured at 63 degrees. Customer "advances" plumbing for visit and adjustment of installation. Meter readings reviewed with customer. | Suspicion |  |  | Customer contacts VVS | /data/reports/71406592_20230512.pdf
328 | 60bf16e47af65fff4fc5ca0f28797b3b5ab8845e12b22446a8e70da305bfa262 | 2023-05-12 | Other (SH) | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt/check-valve fault | Review of facilities. 167 l/h delta t 5. It is estimated that the UFH shunt is the cause. Check valve. (Forward/return?) This shut off and consumption dropped to 0 l/h. Recommended to have a plumber look at it. | Proven |  |  | Customer contacts VVS | /data/reports/71164103_20230512.pdf
329 | 87765b2483b6ce3e4ac38d32e0de98fea6fa9430ee2ebc618a0b0820b2a1f27c | 2023-05-15 | UFH shunt | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt/check-valve fault | Visit to customer regarding poor cooling. Flow = 56 L/h and delta-T = 6 degrees. It is estimated to be a shunt/non-return valve in the underfloor heating installation that is causing poor cooling. The customer contacts VVS to rectify the fault. | Suspicion |  |  | Customer contacts VVS | /data/reports/71784126_20230515.pdf
330 | 82c1c295a0b401f5e01df0717c56a7258eb19054b18a270d66568561ee0018ed | 2023-05-16 | Other (SH) | Other (SH) | 1 | 1 | 1 | 1 | Faulty heating surface in ventilation system | Error on the heating surface of the ventilation system | Proven | 2023-05-13 | 2023-05-15 | Error is resolved | /data/reports/71586010_20230516.pdf
331 | 69d5df83da79da338ef7cb8394dc0b0901e69275d3cf19a0efb93b084c86d9f9 | 2023-05-16 | Other (SH) | Other (SH) | 2 | 1 |  | 3 | Supply temp set down storage tank stopped | Visit due to lack of cooling. Review of facilities. indirect 1 rod plant. Forward flow was 55. Adjusted down. Customer shown where the summer valve is and how the pump can be turned off. Hot water exchanger was avtb at 3. But there was also an electrically heated hot water tank. This was closed and the customer told about the risk of legionella. The customer had the installation reviewed and would like a follow-up later. | Proven |  |  | Error is resolved | /data/reports/71488115_20230516.pdf
332 | 4899ccb13ba61fd4a981324adbdc9544dbfe893807d3d95cdccc0ce19d23dd81 | 2023-05-16 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Possible radiator valve fault DHW temp too high | Visit regarding increasing consumption as well as poor cooling. Probably a radiator valve that was stuck as well as a high set service water temperature cause the problem. The customer himself had gone through the installation and adjusted/exercised the affected components before the visit. Possibly. follow up next week. Meter readings reviewed with customer. | Suspicion |  |  |  | /data/reports/71525324_20230516.pdf
333 | 53769335bc66fb8d166edf31eb9473d638606fb8d4ccefd5e8bd5bf9423d4f5c | 2023-05-22 | UFH shunt | UFH shunt | 2 | 1 | 1 | 3 | UFH check-valve fault | Visit regarding high consumption (230 L/h) and poor cooling (delta-T = 6 degrees). It is estimated to be a non-return valve in the UFH shunt which is the cause of poor cooling. VVS came to the address and is taking action on the problem. Meter and meter readings reviewed with customer. | Suspicion |  |  | Customer contacts VVS | /data/reports/71783743_20230522.pdf
334 | d561667cf97297923eff6b2046aeda58bed8da74aa164e92f6bf36cf7ac5bfc3 | 2023-05-22 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 | 1 | 3 | DHW too high temp | Visit regarding poor cooling. It is considered to be a high set domestic water temp. which causes poor cooling. Flow only through exchanger = 48 L/h and delta-T = 14 degrees. Customer adjusts temp. for hot water exchanger. | Suspicion |  |  |  | /data/reports/71245414_20230522.pdf
335 | 2505e444a1d81b6db017848f9908899a7b9bf003bad6605feaea95d3b15fb228 | 2023-05-22 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | Fluctuating DHW temp and possible heat exchanger fault | Visit regarding fluctuating consumption as well as poor cooling. Customer experiences very hot sometimes fluctuating temperature of service water. In addition not so good cooling over the exchanger when draining hot domestic water. Customer contacts VVS for inspection of installation. | Suspicion |  |  | Customer contacts VVS | /data/reports/71335967_20230522.pdf
336 | d90a6f0dd1a48dcf6b736d24309d9747ebf3ef326f770c8b3191851014221589 | 2023-05-23 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 | 1 | 3 | DHW heat exchanger too high temp | Visits and telephone contact regarding increasing consumption and poor cooling. It is estimated that to be high set temp. to the hot water exchanger which is the cause of the problem. The customer can adjust the temperature himself. | Suspicion |  |  |  | /data/reports/71083212_20230523.pdf
337 | cbc16ef0301714fccd0457a4248900e110a1e38151e6b5ce90e6695ba6d3696f | 2023-05-23 | Other (SH) | UFH shunt | 2 | 1 | 2 | 3 | UFH shunt setting fault | Review of facilities. delta t 3. It is estimated that the UFH shunt setting is the cause of the lack of cooling. Hot water container corroded under the bottom. Recommended to have it replaced. Informed about the possibility of heat+. Has the watts app. | Suspicion |  |  | Customer contacts VVS | /data/reports/71337754_20230523.pdf
338 | 79d41659167e4411ad2d0e02e83d91690e0d37031ac0d9e0f5a1963e9067db25 | 2023-05-24 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | DHW heat exchanger too high temp | Visit regarding poor cooling. Flow = 105 L/h. Delta-T = 10 degrees. At the shut-off for the hot water exchanger flow dropped to 24 L/h. It is estimated to be the domestic water regulator at the exchanger which is the cause of the problem. Customer contacts plumbing for repair of bathroom. Meter readings reviewed with customer. | Suspicion |  |  | Customer contacts VVS | /data/reports/62084094_20230524.pdf
339 | 976a3a9f44a2338db42570100cb93b22cfe935bef941516cf5a2f372002108f9 | 2023-05-30 | Other (SH) | UFH shunt | 2 | 1 | 2 | 3 | UFH shunt fault | Cooling. Review of facilities. It is estimated to be a floor heating shunt in the technical room. This closed down and consumption fell significantly. The customer said that the house is to be renovated soon. | Suspicion |  |  | No action | /data/reports/71525730_20230530.pdf
340 | 1f876d63037c8909a7d34d04cfbb3e21264ee1a6501f5a852c326b4de6bcceb2 | 2023-05-31 | Other (SH) | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | DHW heat exchanger fault | Visit due to high consumption and lack of cooling. Review of facilities. 750 l/h delta t 2. It is estimated that the service water exchanger is the cause. This closed down and consumption fell significantly. Customer will contact VVS. Customer would like a new basket later. | Proven |  |  | Customer contacts VVS | /data/reports/71684113_20230531.pdf
341 | 657fa2bed8335f85b620f28caa424640c8c2ad4b3f3e601c88f03e359979e6af | 2023-05-31 | Other (SH) | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | Heat exchanger fault | Visit due to high consumption and lack of cooling. 780 l/h delta t 2. Review of plant. It is estimated that the change is the cause. Does not shut down. TD recommended to have it adjusted. Recommended to have a plumber look at it. | Proven |  |  | Customer contacts VVS | /data/reports/71165024_20230531.pdf
342 | 36df0cf3ae8ce60e6b0b06a1f9be8aca270f15b31eac6eae26c60ed51bb1ad51 | 2023-06-02 | Other (SH) | DHW regulator - heat exchanger | 2 | 1 | 1 | 1 | DHW heat exchanger fault | Cooling and high consumption. In periods over 600 l/h and almost no cooling. The customer said they could hear a hissing sound and the hot water was very hot. Graph reviewed with the customer. It is estimated that the hot water exchanger is the cause of the lack of cooling. The customer will contact VVS. | Suspicion |  |  | Customer contacts VVS | /data/reports/71078235_20230602.pdf
343 | fd83d66ca5671fd3012049ef3dfcd39975e55b358a0f462cec7806bc39476f96 | 2023-06-06 | Radiator valve | Radiator valve | 2 | 1 | 1 | 1 | Radiator valve without thermostat set too high | Visit due to lack of cooling and large consumption 500 l/h and 3 degrees cooling. Review of installation. It is estimated that the radiator in the basement is the cause - Manually regulated valve without thermostat. This closed and consumption fell to 3 l/h. Customer informed. | Proven |  |  |  | /data/reports/61629814_20230606.pdf
344 | d921c749a011129a582d0e0d4477d7c166ed75ad53c5a0bf52401c2fb193bc8c | 2023-06-07 | Other (SH) | Other (SH) | 2 | 1 | 1 | 3 | Heat exchanger or check-valve fault. Pump stopped | Cooling. 130 l/h delta t 8. Review of plant. Exchanges 48 degrees VV. (Older) UFH shunt. Return from this very hot. This closed down and consumption fell significantly. ( Pump stop ) Customer will contact VVS for review of installation. | Suspicion |  |  | Customer contacts VVS | /data/reports/71078498_20230607.pdf
345 | 37ad66407f6828a334f4f1a5ca5174310e7a3c5e0f75d997d9000c0b19e167e5 | 2023-06-08 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | Radiators set too high | Visit because there were periods of poor cooling. The customer said that the son had moved away from home and he had a good time turning up the radiators. The customer got a copy of the consumption and wanted to show them to his son. | Suspicion |  |  | No action | /data/reports/71587568_20230608.pdf
346 | 9173cca706e86054fb5351de9ef2e8db90633a8b29fad61a500697285c5d722c | 2023-06-13 | Other (SH) | Incorrectly set DHW temperature - storage tank | 2 | 1 | 2 | 3 | Storage tank temp set down | Visit due to lack of cooling. 77 l/h delta t 4. Review of installation together with the customer. It is estimated to be the temperature of the hot water in VVB. Return valve for heating spiral was at max. This adjusted down by the customer. Recommended temperature 55. Consumption dropped to 0 l/h. The customer will contact you later to have a new graph sent. The customer is considering a new exchanger. | Suspicion |  |  | No action | /data/reports/71635298_20230613.pdf
347 | 77f826ec7a684c49fe08ccb8e50385e756a33df8b0e79be41274bcc15fd37c2a | 2023-06-13 | Other (SH) | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | Heat exchanger fault | Visit due to lack of cooling. The customer has adjusted the system himself following a request from the supply. Review of meter and system. Consumption 7 l/h delta t 12. Older termix one exchanger. Idling. Recommended to get this changed. Leaky. Talk about radiators around the house. Floor heating in the bathroom recommended to be as low as possible. Will contact later in the year to have a new basket sent. | Suspicion |  |  | Customer contacts VVS | /data/reports/71078408_20230613.pdf
348 | 616fd7b473f352bfe2f5b4872fa44e78f74cf57f9da324f1e3482fdcd25f9d94 | 2023-06-13 | Other (SH) | Incorrectly set DHW temperature - storage tank | 2 | 1 | 2 | 3 | DHW temp set down | Visit due to lack of cooling. 200 l/h delta t 4. Review of plant. It is considered to be too high temp. on the hot water. Return valve was at max. 55 degrees recommended. This adjusted in and consumption fell significantly. Review of the meter and installation together with the customer. Recommended to change the domestic water circulation pump. General saving advice discussed. Recommended to get watts. | Proven |  |  | Error is resolved | /data/reports/71244713_20230613.pdf
349 | b68a81de548664079cce91f473348d41b4f32d309aa556567c517c82b9859ade | 2023-06-14 | User behaviour | User behaviour | 2 | 1 | 1 | 3 | UFH in bathroom temp too high | Visit due to lack of cooling. Review of facilities. After reviewing the last week's consumption it was concluded that it was most likely manually regulated underfloor heating in the bathroom that was the cause of the lack of cooling Review of the system and meter together with the customer. General heating advice discussed. Recommended to get watts installed. | Suspicion |  |  | Error is resolved | /data/reports/71587629_20230614.pdf
350 | 5aa3516b5b20b1052e87ee10d889201a8291b2bde5cc58851bb231acab8ce9f1 | 2023-06-15 | Other (SH) | Other (SH) | 2 | 2 | 1 | 1 | Pump turned off without adjusting valve | Visit due to lack of cooling. Exchanger and indirect 1st string system. The customer had turned off the pump on the secondary side without adjusting the valve to control the secondary flow down. This adjusted down and ok cooling. General saving advice discussed ( 1st string ) Recommended to get watts | Proven |  |  | Error is resolved | /data/reports/71750403_20230615.pdf
351 | be164a25a22f67adf0c20062b3be00dc7894dbb0e871b4076a0449399a967427 | 2023-06-19 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 | 1 | 1 | DHW temp too high | Domestic water temperature set too high. Review of meter display. Recommended district heating service scheme. Will get in touch later to get a new graph sent by email. | Suspicion |  |  | Error is resolved | /data/reports/71750349_20230620.pdf
352 | fad85c8ffd41701b84b56cd21339328ac47dd821c383965fbf551a0137974f2e | 2023-06-22 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | DHW heat exchanger fault or fouling | Visit to customer regarding poor cooling. It is estimated that the hot water exchanger/regulator is the cause of the problem. Large idle flow through exchanger and delta-T = 2 degrees. In addition more corrosion at exchangers/circulators. Customer contacts VVS. | Suspicion |  |  | Customer contacts VVS | /data/reports/71163505_20230622.pdf
353 | c8c1b6f57a14c851b7393c450b0e4329874f84e2a1ac86a0b10bedff7fcc3521 | 2023-06-22 | Other (SH) | Incorrectly set weather compensation | 2 | 1 | 1 | 3 | Issue with weather compensation indoor temp set down | Lack of cooling. Newer switches with ECL weather compensation. Review of heat curve settings 1.4. min 30 max 70. Temp. changed from 25 to 22. Customer follows consumption and returns. | Suspicion |  |  | No action | /data/reports/71585727_20230622.pdf
354 | fabd425cc56f95197693c1fdefa121387e9f58958b53dd74cc647f8bf5de5921 | 2023-06-28 | Other (SH) | UFH shunt | 2 | 1 | 2 | 3 | Check-valve fault | Defective non-return valve - or the lack of a non-return valve is to blame for a short circuit. | Proven | 2023-06-06 | 2023-06-28 | Customer contacts VVS | /data/reports/71110744_20230628.pdf
355 | b6e00bb2cddd23d22050fc4b850af9d5b2b758517f22f65e1832daf4cc4b181e | 2023-07-06 | Incorrectly set DHW temperature - heat exchanger | Incorrectly set DHW temperature - heat exchanger | 2 | 1 | 1 | 3 | High DHW set temp possible heat exchanger fouling | Visit to customer regarding poor cooling. Approx. 40 L/h idle flow over hot water exchanger. High set temp. of domestic hot water (position 4 5). Customer adjusted temp. down. Insufficient cooling over the exchanger when draining hot domestic water. Customer contacts VVS for check/replacement of hot water exchanger (possible calcification). Meter readings reviewed with customer. | Suspicion |  |  | Customer contacts VVS | /data/reports/71241290_20230706.pdf
356 | b538a2dcf698bc045adfa11cbda6d4d0f8ff443f3df30451b6f232af2d7371d8 | 2023-07-13 | UFH shunt | UFH shunt | 2 | 1 | 1 | 3 | UFH shunt/check-valve fault | Visit to customer regarding poor cooling. Flow = 160 L/h. Delta-T = 4 degrees. It is estimated to be the shunt/check valve for underfloor heating installation which is the cause of the problem. Customer contacts VVS. Meter and meter readings reviewed with customer. | Suspicion |  |  | Customer contacts VVS | /data/reports/71244659_20230713.pdf
357 | d742fb9ec36fb4f04893eb578838b029c1f3a2689aff7bfa2f1af0d682844589 | 2023-07-18 | Other (SH) | UFH shunt | 2 | 1 | 1 | 2 | UFH check-valve fault | Visit due to lack of cooling. Review of installation. It is estimated to be UFH shunt which is the cause of lack of cooling (Contra valve) Customer recommended to get plumbing to do it. Underfloor heating switched off at the ball valve. Meter went to zero. | Suspicion |  |  | Customer contacts VVS | /data/reports/71635455_20230718.pdf
358 | 1c6351c6ce4dc77de7cbe7270e1c700922e4c2180e072ce1e4d60f31bc4e38b3 | 2023-07-18 | Other (DHW) | DHW regulator - heat exchanger | 2 | 2 | 1 | 1 | Heat exchanger fault | Older Indirect plants. It is estimated to be the exchanger for hot water that is the cause of the lack. Recommended service scheme / Heat +. Review of the meter together with the customer. Recommended to have watts installed to monitor consumption. | Suspicion |  |  | Customer contacts VVS | /data/reports/60389258_20230718.pdf
359 | 9aece2bba7a1284da79ad4caf344f73097d2547caa4511ea01e3353d75c1629c | 2023-07-19 | Other (DHW) | Other (DHW) | 2 | 1 | 1 | 3 | AVTB valve (controlling DHW temperature?) set down | Visit high consumption and no cooling. Review of installation. Measures 650 l/h delta t 0.4 on arrival. The customer said that she had a problem with the hot water in the kitchen and an acquaintance had adjusted the system. During review the AVTB for regulating the hot water was turned up to max. The customer recommended 48-50 degrees (About 3 AVTB) After adjustment the consumption dropped to 10 l/h. Measure reviewed and recommended watts and get signed up for the service scheme. | Proven |  |  | Error is resolved | /data/reports/71684155_20230719.pdf
360 | af3de3473e3672846cd5bf7fa825522d400b4e6d08fe4f28428ffa62268c221d | 2023-07-20 | Other (SH) | Other (SH) | 2 | 1 | 1 | 2 | Shunt valve temperature set down | Review of facilities. 200 l/h delta t 6. It is estimated that the valve for controlling the shunt temperature is the cause of the lack of cooling. This was adjusted down by the customer and consumption fell significantly. Recommended to get watts installed on the phone. Recommended review due to corrosion. Will be back for new graph later in the year. | Suspicion |  |  | Error is resolved | /data/reports/71113942_20230720.pdf
361 | 836e70fe2ae9762e8d9a50cc942a4b196703dd38169c3c32b4d2c444d1c45e10 | 2023-07-24 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | Heat exchanger fault | Visit due to lack of cooling high consumption. 1250l/h delta t 4. review of plant. The house is currently rented out. It is estimated that a defective exchanger is the cause. Owner of the house informed and will contact a plumber. | Proven |  |  | Customer contacts VVS | /data/reports/71784972_20230724.pdf
362 | 81ad37f88757354c5a11d06d82fb340afd7c52b222133dc2b1a6415434407c19 | 2023-08-02 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 |  |  | Proven |  |  | Customer contacts VVS | /data/reports/71076881_20230802.pdf
363 | ce01fb88175815d3fa0c0a18fdad4ddd6632e85e07c1e82b58f9417dfeb98b69 | 2023-08-07 | Other (DHW) | Other (DHW) | 2 | 1 | 1 | 3 | Dirt collector or heat exchanger fault | Review of facilities. 125 l/h delta t 6. Hot water regulator was at max. 175 l/h at consumption 43 degrees. Possibly dirt collector / exchanger. Recommended to get plumbing for system review. | Suspicion |  |  | Customer contacts VVS | /data/reports/71509097_20230807.pdf
364 | c169a4addf356f06fdf96fecd6c84516f3ca793b8ca6a0ed20c84a73de274451 | 2023-08-11 | Other (SH) | Other (SH) | 2 | 2 | 2 | 2 | Plant valve temp too high | Visit due to lack of cooling high consumption. Read 220 l/h delta t 6. Review of plant. Indirect plant valve for temp. secondary temp was high. Recommended to adjust it. After adjustment consumption fell to around 30 l/h. Recommended to adjust valve summer - autumn - winter. Get card if there are any further questions. | Suspicion |  |  | Error is resolved | /data/reports/71539333_20230811.pdf
365 | afe72b6be244807f295eeea4fac6762b85dac599711c62c44cf1c40623f1dbf2 | 2023-08-11 | Towel dryer | Towel dryer | 2 | 1 | 1 | 3 | Towel dryer high temp | Visit due to lack of cooling in periods. It is estimated that the use of towel dryers is the cause. Review of plant and the various components. Recommended constant pressure pump on shunt. Various saving advice discussed. The customer has watts. The house is being remodeled but will have the plumbers check the pre-setting on the radiators and whether the shunt hose lengths are adjusted correctly. | Proven |  |  | Customer contacts VVS | /data/reports/71750273_20230811.pdf
366 | e8782fae0823e4535faf3eebde24e14dde93db2e6fb0beb0ac0093972e960c91 | 2023-08-11 | Other (DHW) | Other (DHW) | 2 | 1 | 1 | 3 | Test | Testing | Suspicion | 2023-05-01 |  | No action | /data/reports/71245411_20230811.pdf
367 | fcaf19b1c2f43c34466e3ca94dc40d745af396eec2cda0ce64bba99387216997 | 2023-08-14 | UFH shunt | UFH shunt | 2 | 1 | 1 | 2 |  |  | Suspicion |  |  | Customer contacts VVS | /data/reports/71683987_20230814.pdf
368 | 1cb431d7bf353abf3b3bb5f765b03cdf205c141c3843eac7f9bc7d4fadc7c8c5 | 2023-08-18 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 |  | DHW faulty tpv valve | Lack of cooling - high consumption. Review of facilities. The hot water gets very hot. It is estimated to be a TPV valve for controlling the hot water. Exchanges closed and consumption fell significantly. Customer contacts VVS | Proven |  |  | Customer contacts VVS | /data/reports/71586714_20230818.pdf
369 | 3e3c272afb7a9b27f1f0655643b9a8402f8ae914182c69273ad453f5bf4d02af | 2023-08-21 | Other (SH) | Other (SH) | 2 | 1 | 1 | 2 | UFH valve set down | Visit due to lack of cooling. 150 l/h delta t 1.Review of system newer hot water exchanger and UFH shunt. It is estimated to be a valve for underfloor heating that was turned up high this was set to 35-38 and liters dropped to 0. | Proven |  |  | Error is resolved | /data/reports/71242092_20230821.pdf
370 | 47db658ceea13d9b66dca4334b270741f0840be0d9863a2ad77662a005fe1704 | 2023-08-23 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | Heat exchanger fault | Customer alerted to high consumption and lack of cooling. It is considered to be the bill of exchange that is the cause. The customer has contacted VVS. | Proven |  |  | Customer contacts VVS | /data/reports/71585514_20230823.pdf
371 | a59079cb7841222dcf088aa9e1dfcb6e5777b8b1e6c5f66c5100283bb22cf4ec | 2023-08-23 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 2 | DHW faulty tpv valve | Lack of cooling and high consumption. 150 l/h delta t 1. Review of plant. Newer installation with ecl 110 and tpv valve for hot water regulation. It is estimated to be a defective tpv valve which is the cause of the lack of cooling. The customer handles the plumbing. Will contact you later for a new graph when the system is put in order. | Proven |  |  | Customer contacts VVS | /data/reports/61629809_20230823.pdf
372 | 164136fdfc742eaced7251985056f31bb9e0e1406b0041c72bcf9d269cc5456c | 2023-08-28 | Towel dryer | Towel dryer | 2 | 1 | 2 | 3 | Towel dryer high temp | Visit due to periods of lack of cooling and high consumption. Review of facilities. Hot water tank radiator and heated towel rail. It is estimated that the use of a towel dryer is the cause of the lack of cooling. Recommended to turn it down and install a pressure difference regulator on the system. | Suspicion |  |  | Customer contacts VVS | /data/reports/71244748_20230828.pdf
373 | 60e4a6c0b15cb57023138c83b639ad7b40bc290ca4c18c8a0a602c28fad8119d | 2023-08-28 | Other (SH) | User behaviour | 2 | 1 | 1 | 3 | Usage recommendations | In connection with routine inspections. Review of plant and installation in data warehouse. In the summer period slightly above expected return. Possibly circulation on the hot water. Recommended to try and install timer. UFH shunt recommended to turn down in summer. Smart thermostats recommended to keep an eye on the battery level. | Suspicion |  |  | No action | /data/reports/71586125_20230829.pdf
374 | 1e9f7034ea6fded1fe26b215e6f85920123437a8cea5f4f49fb7c5d92489fcec | 2023-09-04 | Other (SH) | User behaviour | 2 | 1 | 1 | 1 | User behaviour | Visit due to lack of cooling and high consumption. Review of facilities. It is considered to be User behaviour in connection with summer closure. Review of meter functions. General talk about heat utilization. | Suspicion |  |  | Error is resolved | /data/reports/71523623_20230904.pdf
375 | 0f3a38660a81f66e98ffbf7e03e0641009ea860e3f4e96b8f001b2d6c1ad7267 | 2023-09-04 | Other (SH) | User behaviour | 2 | 1 | 1 | 3 | Tradesmen behaviour | Visit due to high consumption and no cooling. Customer not at home but craftsmen were on site. Tried calling the customer. The customer called back and I recommended having tradesmen close until the customer could go through the installation later. | Suspicion |  |  | No action | /data/reports/71586777_20230904.pdf
376 | 6389be4ab730a24775ea6802910e9cb7961581b10e8cce642ef3887685285515 | 2023-09-04 | Other (SH) | DHW regulator - heat exchanger | 2 | 1 | 1 | 2 | DHW control valve issue | Visit because there is a lack of cooling at times. The customer said that the hot water was very hot even though it is set to 52 degrees. Wavin electronically controlled valve. The customer will follow the installation and contact VVS. | Suspicion |  |  | Customer contacts VVS | /data/reports/71374231_20230904.pdf
377 | 27d6af6b010b9c4988a3519b7001371f4f650477dd01d6fa9b2ce84bd447647c | 2023-09-06 | Towel dryer | Towel dryer | 2 | 1 | 1 | 3 | Towel dryer temp set down | Visit to customer regarding increasing consumption as well as poor cooling. Flow = 180 L/h. Delta-T = 2 degrees. High setting towel dryer is considered to be the cause of the problem. At the towel dryer cubicle flow dropped to 3 L/h. The cooling is then expected to stabilize. Meter readings reviewed with the customer. | Proven |  |  | Error is resolved | /data/reports/71112502_20230906.pdf
378 | 3de37b8b06289dd7764955e201619c0ac1a4c312f1f9cfc641005d43449285a9 | 2023-09-07 | DHW regulator - heat exchanger | DHW regulator - heat exchanger | 2 | 1 | 1 | 3 | DHW regulator fault | Visit to customer regarding poor cooling. It is estimated that the domestic water regulator is the cause of the problem. Customer contacts VVS. | Suspicion |  |  | Customer contacts VVS | /data/reports/71683635_20230907.pdf
379 | 9eec8808b1a6d41249d6d84a084d564154764f08615df3aafcbf2465e3c13d6e | 2023-09-12 | Other (SH) | Other (SH) | 2 | 1 | 1 |  | Smart thermostat battery issue | Contacted over the phone due to high consumption and lack of cooling. It is estimated to be a smart thermostat that is the cause. The customer wants to change the battery. | Suspicion |  |  | Error is resolved | /data/reports/71083136_20230912.pdf
380 | d58afd20643e9e647eec3ade4b683fe999e136f4bd64a38e86785f7a5262e6a4 | 2023-09-12 | Other (SH) | Towel dryer | 2 | 1 |  |  | Towel dryer high temp | Contacted over the phone. The customer informed about the lack of cooling and was able to tell that it might be a towel dryer that is the cause. | Suspicion |  |  | Error is resolved | /data/reports/71524615_20230912.pdf
381 | 88e69b13c7bfc0f543b1c4d81c86687461b93e1cc2d27be0786e22ee7674363d | 2023-09-12 | Other (SH) | Towel dryer | 2 | 1 | 2 | 3 | Towel dryer temp set down | Visit due to lack of cooling. Review of facilities. Radiators in rooms. Underfloor heating in bathrooms. Towel dryer recommended to adjust slightly down. Older ( 1987) VVB with temp. at 65 degrees. Recommended to adjust it down to 55-58 degrees. Domestic water circulation. Recommended to install a timer. Review of the meter together with the customer. Talk about the possibility of heating + Follow up visit on Friday 22/9 to see if adjustments have had the desired effect. | Proven |  |  | No action | /data/reports/71549931_20230912.pdf
382 | 13aefe279835a16c878797420d04075def5ca969625892da0448b96835c0dc99 | 2023-09-13 | Other (DHW) | DHW regulator - heat exchanger | 2 | 1 | 1 | 1 | Heat exchanger fault | Contacted due to lack of cooling. It is considered to be an exchange for the hot water which is the cause. The customer will change bills and return to have a new graph sent. The customer has several houses in the city and would like to have them looked after. Will contact you later. | Proven |  |  | Customer contacts VVS | /data/reports/71784545_20230913.pdf